## Annual Energy Production
Annual Energy Potential (MWH)
Site | Head (FT) | Standard Instream Flows | Half Instream Flows | No Instream Flows
Turners
A | 14.5 | 715.4487 | 715.4487 | 715.4487
B | 22 | 455.6895 | 625.9569 | 1049.7937
C | 38 | 830.8922 | 1137.468 | 1888.9442
Hunts
D | 8.5 | 400.0383 | 400.0383 | 400.0383
E | 23.5 | 524.1768 | 717.0678 | 1184.4762
E-2 | 23.5 | 463.9286 | * | 815
Omega
F | 8 | 373.7541 | 373.7541 | 373.7541

## Economics Standard IF
Economic Analysis - Standard Instream Flows
Site | Installed Costs ($1,000's) | Installed Capacity (kW) | $/kW | IRR | NPV ($1,000's)
Turners
A | 3326.1607 | 204.5021 | 16264.6781 | 2.521% | -665.4101
B | 4366.404 | 155.6141 | 28059.1888 | #DIV/0! | -3072.8713
C | 4720.7116 | 287.6502 | 16411.2918 | -1.156% | -1858.3048
Hunts
D | 3363.7447 | 111.6471 | 30128.3692 | #DIV/0! | -2313.955
E | 3325.6498 | 184.0843 | 18065.9021 | #NUM! | -1707.4858
Omega
F | 3276.9127 | 103.9092 | 31536.3183 | #DIV/0! | -2293.6661

## Economics Half IF
Economic Analysis - Half Instream Flows
Site | Installed Costs ($1,000's) | Installed Capacity (kW) | $/kW | IRR | NPV ($1,000's)
Turners
A | 3326.1607 | 204.5021 | 16264.6781 | 2.521% | -665.4101
B | 4626.1805 | 176.278 | 26243.6668 | #DIV/0! | -2852.0124
C | 4976.0082 | 326.4159 | 15244.3819 | 3.71% | -558.8563
Hunts
D | 3363.7447 | 111.6471 | 30128.3692 | #DIV/0! | -2313.955
E | 3519.012 | 208.6515 | 16865.5038 | 1.614% | -908.581
Omega
F | 3276.9127 | 103.9092 | 31536.3183 | #DIV/0! | -2293.6661

## Economics No IF
Economic Analysis - No Instream Flows
Site | Installed Costs ($1,000's) | Installed Capacity (kW) | $/kW | IRR | NPV ($1,000's)
Turners
A | 3326.1607 | 204.5021 | 16264.6781 | 2.521% | -665.4101
B | 5433.7794 | 287.6978 | 18887.1112 | 0.9488% | -1596.6953
C | 5837.7521 | 533.6683 | 10938.914 | 8.674% | 2450.172
Hunts
D | 3363.7447 | 111.6471 | 30128.3692 | #DIV/0! | -2313.955
E | 4019.7894 | 340.7352 | 11797.4013 | 7.303% | 985.1931
E-2 | 2994 | 271 | 11064 | 6% | 246
Omega
F | 3276.9127 | 103.9092 | 31536.3183 | #DIV/0! | -2293.6661

## Hunts Mill Options
Hunts Mill Options - Standard Instream Flows
Development | Installed Costs ($1,000's) | Installed Capacity (kW) | Annual Energy (MWH) | $/kW | IRR | NPV ($1,000's)
1. Diversion from Turners (C)
a. New Equipment | 4720.7116 | 287.6502 | 830.8922 | 16411.2918 | -1.156% | -1858.3048
b. Repower Existing Unit | 4211.9854 | 282.2584 | 742.5588 | 14922.4459 | -1.231% | -1675.1166
2. Diversion from Hunts Mill Dam (E)
a. New Equipment | 3325.6498 | 184.0843 | 524.1768 | 18065.9021 | #NUM! | -1707.4858
b. Repower Existing Unit | 2836.3636 | 178.0491 | 463.9286 | 15930.2361 | #NUM! | -1396.5901
b. Restore Existing Turbine | 2703.3432 | 110.0337 | 334.8396 | 24568.317 | #DIV/0! | -1874.5144

## Summary - Cash
ID | Project / Description
A | Turner Reservoir
B | Turner - Hunt's Mill
C | Turner - Hunt's Mill 2 |  | C-2 | w/ repowered unit
D | Hunt's Mill
E | Hunt's Mill 2 |  | E-2 | w/ repowered unit |  |  | E-3 | w/ restored unit
F | Omega Pond
All Alts
| Escalation Rate | 2.5% |  | Discount Rate | 5% |  |  | Denotes cells for user input
| REC's ($//MWH) | 25 |  | Term (Yrs) | 20
Results With Instream Flows
Alt | Installed Cost ($1,000's) | Installed Capacity (kW) | Installed Costs ($/kw) | Energy (MWH) | RI Grants | Fed Grant | Energy Rate $/MWH | IRR (%) | NPV ($1,000s)
A | 3326.1607 | 204.5021 | 16264.6781 | 715.4487 | 25% | 15% | 125 | 2.521% | -665.4101
B | 4366.404 | 155.6141 | 28059.1888 | 455.6895 | 25% | 15% | 125 | #DIV/0! | -3072.8713
C | 4720.7116 | 287.6502 | 16411.2918 | 830.8922 | 25% | 15% | 125 | -1.156% | -1858.3048
C-2 | 4211.9854 | 282.2584 | 14922.4459 | 742.5588 | 25% | 15% | 125 | -1.231% | -1675.1166
D | 3363.7447 | 111.6471 | 30128.3692 | 400.0383 | 25% | 15% | 125 | #DIV/0! | -2313.955
E | 3325.6498 | 184.0843 | 18065.9021 | 524.1768 | 25% | 15% | 125 | #NUM! | -1707.4858
E-2 | 2836.3636 | 178.0491 | 15930.2361 | 463.9286 | 25% | 15% | 125 | #NUM! | -1396.5901
E-3 | 2703.3432 | 110.0337 | 24568.317 | 334.8396 | 25% | 15% | 125 | #DIV/0! | -1874.5144
F | 3276.9127 | 103.9092 | 31536.3183 | 373.7541 | 25% | 15% | 125 | #DIV/0! | -2293.6661
Results with 1/2 Instream Flows
Alt | Installed Cost ($1,000's) | Installed Capacity (kW) | Installed Costs ($/kw) | Energy (MWH) | RI Grants | Fed Grant | Energy Rate $/MWH | IRR | NPV ($1,000s)
B | 4626.1805 | 176.278 | 26243.6668 | 625.9569 | 25% | 15% | 125 | #DIV/0! | -2852.0124
C | 4976.0082 | 326.4159 | 15244.3819 | 1137.468 | 25% | 15% | 125 | 3.71% | -558.8563
E | 3519.012 | 208.6515 | 16865.5038 | 717.0678 | 25% | 15% | 125 | 1.614% | -908.581
Results with No Instream Flows
Alt | Installed Cost ($1,000's) | Installed Capacity (kW) | Installed Costs ($/kw) | Energy (MWH) | RI Grants | Fed Grant | Energy Rate $/MWH | IRR | NPV ($1,000s)
B | 5433.7794 | 287.6978 | 18887.1112 | 1049.7937 | 25% | 15% | 125 | 0.9488% | -1596.6953
C | 5837.7521 | 533.6683 | 10938.914 | 1888.9442 | 25% | 15% | 125 | 8.674% | 2450.172
E | 4019.7894 | 340.7352 | 11797.4013 | 1184.4762 | 25% | 15% | 125 | 7.303% | 985.1931
E-2 | 2994.3648 | 270.634 | 11064.2612 | 814.6396 | 25% | 15% | 125 | 5.807% | 245.6962
Notes:
1 | RI (State) Grants: defined % of Direct Costs
2 | Fed Grant: Assumes extension of Investment Tax Credit (ITC) & assocaited muni. benefit of partnership with outside tax investor
3 | Energy Rate: assumes pricing for distributed renewable energy
4 | IRR: Internal Rate of Return
5 | NPV (Net Present Value): values given represent NPV at end of study period
6 | Estimates based on 20 year study period.
7 | REC (Renewable Energy Certificate): additional commodity value for energy derived from qualified renewable sources

## Energy
Results w/ Instream Flows
ID | Site | BM | HW | TW | D.A. (SqMi) | Gross Head (ft) | Hyd.Cap (cfs) | Installed Capacity (kw) | Net Annual Energy (MWH) | Capacity Factor | Runner Dia Meters | Penstk Dia Ft. | Equipment Configuration
A | Turners Reservoir Dam | 52.55 | 47.55 | 33.05 | 48 | 14.5 | 213 | 204.5021 | 715.4487 | 39.94% | 1.25 | 5.8224 | Horz Tube
B | Turner - Hunt's Mill | see notes | 47.55 | 25.55 | 48 | 22 | 114 | 155.6141 | 455.6895 | 33.43% | 0.9 | 4.2595 | Horz Tube
C | Turner - Hunt's Mill 2 | see notes | 47.6 | 11 | 48 | 38 | 114 | 287.6502 | 830.8922 | 32.97% | 0.9 | 4.2595 | Vert Kaplan
C-2 | Turner - Hunt's Mill 2 (Repowered Francis) |  |  |  | 48 | 38 | 114 | 282.2584 | 742.5588 | 30.03% | 0.92 | 4.2595 | Vert Francis
D | Hunt's Mill Dam | 37.95 | 33.95 | 25.55 | 53 | 8.5 | 213 | 111.6471 | 400.0383 | 39.94% | 1.25 | 5.8224 | Horz Tube
E | Hunt's Mill Dam 2 | 38 | 34 | 7.8 | 53 | 23.5 | 114 | 184.0843 | 524.1768 | 32.51% | 0.9 | 4.2595 | Horz Tube
E-2 | Hunt's Mill Dam 2 (Repowered Francis) |  |  |  | 53 | 23.5 | 114 | 178.0491 | 463.9286 | 29.74% | 0.9 | 4.2595 | Vert Francis
E-3 | Hunt's Mill Dam 2 (Restored Francis) |  |  |  | 53 | 23.5 | 84 | 110.0337 | 334.8396 | 34.74% | 0.813 | 3.6564 | Vert Francis
F | Omega Pond Dam | 14.8 | 10.05 | 1.9 | 56 | 8 | 213 | 103.9092 | 373.7541 | 39.94% | 1.25 | 5.8224 | Horz Tube
Results w. 1/2 Instream Flows
ID | Site | BM | HW | TW | D.A. (SqMi) | Gross Head (ft) | Hyd.Cap (cfs) | Installed Capacity (kw) | Net Annual Energy (MWH) | Capacity Factor | Runner Dia Meters | Penstk Dia Ft. | Equipment Configuration | Hyd | Runner | penstock
B | Turner - Hunt's Mill | see notes | #REF! | #REF! | 48 | 22 | 130 | 176.278 | 625.9569 | 40.54% | 0.95 | 4.5486 | Horz Tube | 114 | 0.9 | 4.26
C | Turner - Hunt's Mill 2 | see notes | 47.6 | 11 | 48 | 38 | 130 | 326.4159 | 1137.468 | 39.78% | 0.95 | 4.5486 | Vert Kaplan | 130 | 0.95 | 4.55
E | Hunt's Mill Dam 2 | 38 | 34 | 7.8 | 53 | 23.5 | 130 | 208.6515 | 717.0678 | 39.23% | 0.95 | 4.5486 | Horz Tube | 174 | 1.1172 | 5.2135
[14 empty] | 213 | 1.25 | 5.82
Results w. No Instream Flows
ID | Site | BM | HW | TW | D.A. (SqMi) | Gross Head (ft) | Hyd.Cap (cfs) | Installed Capacity (kw) | Net Annual Energy (MWH) | Capacity Factor | Runner Dia Meters | Penstk Dia Ft. | Equipment Configuration
B | Turner - Hunt's Mill | see notes | #REF! | #REF! | 48 | 22 | 213 | 287.6978 | 1049.7937 | 41.65% | 1.25 | 5.8224 | Horz Tube
C | Turner - Hunt's Mill 2 | see notes | 47.6 | 11 | 48 | 38 | 213 | 533.6683 | 1888.9442 | 40.41% | 1.25 | 5.8224 | Vert Kaplan
E | Hunt's Mill Dam 2 | 38 | 34 | 7.8 | 53 | 23.5 | 213 | 340.7352 | 1184.4762 | 39.68% | 1.25 | 5.8224 | Horz Tube
E-2 | Hunt's Mill 2 (Repowered Francis) |  |  |  | 53 | 23.5 | 174 | 270.634 | 814.6396 | 38.3% | 1.12 | 5.21 | Vert Francis

## Proforma A
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 3326.1607
b | O&M |  | 11 | 11.275 | 11.5569 | 11.8458 | 12.142 | 12.4455 | 12.7567 | 13.0756 | 13.4025 | 13.7375 | 14.081 | 14.433 | 14.7938 | 15.1637 | 15.5427 | 15.9313 | 16.3296 | 16.7378 | 17.1563 | 17.5852
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 8.5233 | 8.7364 | 8.9548 | 9.1786 | 9.4081 | 9.6433 | 9.8844 | 10.1315 | 10.3848 | 10.6444 | 10.9105 | 11.1833 | 11.4629 | 11.7494 | 12.0432 | 12.3443 | 12.6529 | 12.9692 | 13.2934 | 13.6258
e | Payment in lieu of Property Taxes |  | 51.1397 | 52.4182 | 53.7287 | 55.0719 | 56.4487 | 57.8599 | 59.3064 | 60.7891 | 62.3088 | 63.8665 | 65.4632 | 67.0997 | 68.7772 | 70.4967 | 72.2591 | 74.0656 | 75.9172 | 77.8151 | 79.7605 | 81.7545
f
g | Subtotal, Costs | 3326.1607 | 70.663 | 72.4296 | 74.2403 | 76.0964 | 134.5692 | 79.9487 | 81.9475 | 83.9961 | 86.096 | 216.2569 | 90.4547 | 92.716 | 95.0339 | 97.4098 | 172.2599 | 102.3411 | 104.8997 | 107.5222 | 110.2102 | 276.8271
2 | Revenues ($1,000's)
a | State Grants | 831.5402
b | Federal Grants | 498.9241
c | Energy |  | 91.6669 | 93.9585 | 96.3075 | 98.7152 | 101.1831 | 103.7127 | 106.3055 | 108.9631 | 111.6872 | 114.4794 | 117.3413 | 120.2749 | 123.2818 | 126.3638 | 129.5229 | 132.761 | 136.08 | 139.482 | 142.969 | 146.5433
d | Recs |  | 18.3334 | 18.7917 | 19.2615 | 19.743 | 20.2366 | 20.7425 | 21.2611 | 21.7926 | 22.3374 | 22.8959 | 23.4683 | 24.055 | 24.6564 | 25.2728 | 25.9046 | 26.5522 | 27.216 | 27.8964 | 28.5938 | 29.3087
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 2515.4577
h | Subtotal, Revenues | 1330.4643 | 110.0002 | 112.7503 | 115.569 | 118.4582 | 121.4197 | 124.4552 | 127.5666 | 130.7557 | 134.0246 | 137.3752 | 140.8096 | 144.3299 | 147.9381 | 151.6366 | 155.4275 | 159.3132 | 163.296 | 167.3784 | 171.5628 | 2691.3096
2725.1508
3 | Cashflows ($1,000's) | [21 empty] | 2515.4577
a | Nominal Dollars | -1995.6964 | 39.3372 | 40.3206 | 41.3287 | 42.3619 | -13.1495 | 44.5064 | 45.6191 | 46.7596 | 47.9286 | -78.8817 | 50.355 | 51.6138 | 52.9042 | 54.2268 | -16.8325 | 56.972 | 58.3963 | 59.8562 | 61.3526 | 2414.4825
b | NPV | -1995.6964 | 37.464 | 36.572 | 35.7013 | 34.8512 | -10.303 | 33.2114 | 32.4206 | 31.6487 | 30.8952 | -48.4265 | 29.4415 | 28.7405 | 28.0562 | 27.3882 | -8.0967 | 26.0995 | 25.4781 | 24.8715 | 24.2793 | 909.9931
c | Cum NPV | -1995.6964 | -1958.2324 | -1921.6604 | -1885.9591 | -1851.1079 | -1861.4109 | -1828.1995 | -1795.7788 | -1764.1301 | -1733.2349 | -1781.6614 | -1752.2199 | -1723.4794 | -1695.4232 | -1668.035 | -1676.1317 | -1650.0321 | -1624.554 | -1599.6825 | -1575.4032 | -665.4101
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 715.4487 |  | Max KW | 204.5021 |  | State Grants | 831.5402 |  | Fed Grants | 498.9241
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | 2.521% |  | Cum NPV | -665.4101 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma B
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 4366.404
b | O&M |  | 7.0062 | 7.1814 | 7.3609 | 7.5449 | 7.7336 | 7.9269 | 8.1251 | 8.3282 | 8.5364 | 8.7498 | 8.9686 | 9.1928 | 9.4226 | 9.6582 | 9.8996 | 10.1471 | 10.4008 | 10.6608 | 10.9273 | 11.2005
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 11.1889 | 11.4686 | 11.7553 | 12.0492 | 12.3505 | 12.6592 | 12.9757 | 13.3001 | 13.6326 | 13.9734 | 14.3228 | 14.6808 | 15.0478 | 15.424 | 15.8096 | 16.2049 | 16.61 | 17.0253 | 17.4509 | 17.8872
e | Payment in lieu of Property Taxes |  | 67.1335 | 68.8118 | 70.5321 | 72.2954 | 74.1028 | 75.9553 | 77.8542 | 79.8006 | 81.7956 | 83.8405 | 85.9365 | 88.0849 | 90.287 | 92.5442 | 94.8578 | 97.2293 | 99.66 | 102.1515 | 104.7053 | 107.3229
f
g | Subtotal, Costs | 4366.404 | 85.3286 | 87.4618 | 89.6484 | 91.8896 | 150.7572 | 96.5415 | 98.955 | 101.4289 | 103.9646 | 234.5722 | 109.2278 | 111.9585 | 114.7575 | 117.6264 | 192.982 | 123.5813 | 126.6708 | 129.8376 | 133.0835 | 300.2722
2 | Revenues ($1,000's)
a | State Grants | 1091.601
b | Federal Grants | 654.9606
c | Energy |  | 58.3852 | 59.8448 | 61.341 | 62.8745 | 64.4464 | 66.0575 | 67.7089 | 69.4017 | 71.1367 | 72.9151 | 74.738 | 76.6065 | 78.5216 | 80.4847 | 82.4968 | 84.5592 | 86.6732 | 88.84 | 91.061 | 93.3375
d | Recs |  | 11.677 | 11.969 | 12.2682 | 12.5749 | 12.8893 | 13.2115 | 13.5418 | 13.8803 | 14.2273 | 14.583 | 14.9476 | 15.3213 | 15.7043 | 16.0969 | 16.4994 | 16.9118 | 17.3346 | 17.768 | 18.2122 | 18.6675
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 0
h | Subtotal, Revenues | 1746.5616 | 70.0623 | 71.8138 | 73.6092 | 75.4494 | 77.3356 | 79.269 | 81.2507 | 83.282 | 85.3641 | 87.4982 | 89.6856 | 91.9278 | 94.2259 | 96.5816 | 98.9961 | 101.471 | 104.0078 | 106.608 | 109.2732 | 112.005
3577.4307
3 | Cashflows ($1,000's) | [21 empty] | -976.2216
a | Nominal Dollars | -2619.8424 | -15.2663 | -15.648 | -16.0392 | -16.4402 | -73.4216 | -17.2725 | -17.7043 | -18.1469 | -18.6006 | -147.074 | -19.5422 | -20.0308 | -20.5315 | -21.0448 | -93.9859 | -22.1102 | -22.663 | -23.2295 | -23.8103 | -188.2672
b | NPV | -2619.8424 | -14.5394 | -14.1932 | -13.8553 | -13.5254 | -57.5277 | -12.889 | -12.5821 | -12.2825 | -11.9901 | -90.2907 | -11.4259 | -11.1539 | -10.8883 | -10.6291 | -45.2088 | -10.1289 | -9.8878 | -9.6524 | -9.4225 | -70.9559
c | Cum NPV | -2619.8424 | -2634.3818 | -2648.575 | -2662.4302 | -2675.9556 | -2733.4834 | -2746.3723 | -2758.9544 | -2771.237 | -2783.227 | -2873.5177 | -2884.9437 | -2896.0975 | -2906.9859 | -2917.6149 | -2962.8237 | -2972.9527 | -2982.8404 | -2992.4928 | -3001.9153 | -3072.8713
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 455.6895 |  | Max KW | 155.6141 |  | State Grants | 1091.601 |  | Fed Grants | 654.9606
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | #DIV/0! |  | Cum NPV | -3072.8713 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma B (no min flow)
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 5433.7794
b | O&M |  | 16.1406 | 16.5441 | 16.9577 | 17.3816 | 17.8162 | 18.2616 | 18.7181 | 19.1861 | 19.6657 | 20.1574 | 20.6613 | 21.1778 | 21.7073 | 22.25 | 22.8062 | 23.3764 | 23.9608 | 24.5598 | 25.1738 | 25.8031
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 13.9241 | 14.2722 | 14.629 | 14.9947 | 15.3696 | 15.7538 | 16.1476 | 16.5513 | 16.9651 | 17.3892 | 17.824 | 18.2696 | 18.7263 | 19.1945 | 19.6743 | 20.1662 | 20.6703 | 21.1871 | 21.7168 | 22.2597
e | Payment in lieu of Property Taxes |  | 83.5444 | 85.633 | 87.7738 | 89.9681 | 92.2173 | 94.5228 | 96.8858 | 99.308 | 101.7907 | 104.3355 | 106.9438 | 109.6174 | 112.3579 | 115.1668 | 118.046 | 120.9971 | 124.0221 | 127.1226 | 130.3007 | 133.5582
f
g | Subtotal, Costs | 5433.7794 | 113.609 | 116.4492 | 119.3605 | 122.3445 | 181.9735 | 128.5382 | 131.7516 | 135.0454 | 138.4215 | 269.8905 | 145.4291 | 149.0648 | 152.7915 | 156.6113 | 232.9414 | 164.5397 | 168.6532 | 172.8695 | 177.1913 | 345.4827
2 | Revenues ($1,000's)
a | State Grants | 1358.4448
b | Federal Grants | 815.0669
c | Energy |  | 134.5048 | 137.8674 | 141.3141 | 144.847 | 148.4682 | 152.1799 | 155.9844 | 159.884 | 163.8811 | 167.9781 | 172.1775 | 176.482 | 180.894 | 185.4164 | 190.0518 | 194.8031 | 199.6732 | 204.665 | 209.7816 | 215.0262
d | Recs |  | 26.901 | 27.5735 | 28.2628 | 28.9694 | 29.6936 | 30.436 | 31.1969 | 31.9768 | 32.7762 | 33.5956 | 34.4355 | 35.2964 | 36.1788 | 37.0833 | 38.0104 | 38.9606 | 39.9346 | 40.933 | 41.9563 | 43.0052
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 3056.4139
h | Subtotal, Revenues | 2173.5118 | 161.4058 | 165.4409 | 169.577 | 173.8164 | 178.1618 | 182.6158 | 187.1812 | 191.8608 | 196.6573 | 201.5737 | 206.6131 | 211.7784 | 217.0728 | 222.4997 | 228.0622 | 233.7637 | 239.6078 | 245.598 | 251.7379 | 3314.4453
4451.9401
3 | Cashflows ($1,000's) | [21 empty] | 3056.4139
a | Nominal Dollars | -3260.2676 | 47.7968 | 48.9917 | 50.2165 | 51.4719 | -3.8117 | 54.0777 | 55.4296 | 56.8154 | 58.2357 | -68.3168 | 61.1839 | 62.7135 | 64.2814 | 65.8884 | -4.8793 | 69.224 | 70.9546 | 72.7285 | 74.5467 | 2968.9626
b | NPV | -3260.2676 | 45.5208 | 44.4369 | 43.3789 | 42.3461 | -2.9866 | 40.3536 | 39.3928 | 38.4549 | 37.5393 | -41.9406 | 35.773 | 34.9212 | 34.0898 | 33.2781 | -2.347 | 31.7123 | 30.9573 | 30.2202 | 29.5007 | 1118.9708
c | Cum NPV | -3260.2676 | -3214.7469 | -3170.31 | -3126.9311 | -3084.585 | -3087.5715 | -3047.218 | -3007.8252 | -2969.3703 | -2931.831 | -2973.7716 | -2937.9986 | -2903.0774 | -2868.9876 | -2835.7095 | -2838.0565 | -2806.3442 | -2775.3869 | -2745.1667 | -2715.6661 | -1596.6953
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 1049.7937 |  | Max KW | 287.6978 |  | State Grants | 1358.4448 |  | Fed Grants | 815.0669
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | 0.9488% |  | Cum NPV | -1596.6953 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma B (1-2 min flow)
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 4626.1805
b | O&M |  | 9.6241 | 9.8647 | 10.1113 | 10.3641 | 10.6232 | 10.8888 | 11.161 | 11.44 | 11.726 | 12.0192 | 12.3196 | 12.6276 | 12.9433 | 13.2669 | 13.5986 | 13.9385 | 14.287 | 14.6442 | 15.0103 | 15.3855
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 11.8546 | 12.151 | 12.4547 | 12.7661 | 13.0852 | 13.4124 | 13.7477 | 14.0914 | 14.4437 | 14.8048 | 15.1749 | 15.5542 | 15.9431 | 16.3417 | 16.7502 | 17.169 | 17.5982 | 18.0382 | 18.4891 | 18.9513
e | Payment in lieu of Property Taxes |  | 71.1275 | 72.9057 | 74.7284 | 76.5966 | 78.5115 | 80.4743 | 82.4861 | 84.5483 | 86.662 | 88.8285 | 91.0492 | 93.3255 | 95.6586 | 98.0501 | 100.5013 | 103.0139 | 105.5892 | 108.2289 | 110.9347 | 113.708
f
g | Subtotal, Costs | 4626.1805 | 92.6062 | 94.9214 | 97.2944 | 99.7267 | 158.7903 | 104.7754 | 107.3948 | 110.0797 | 112.8317 | 243.6609 | 118.5438 | 121.5074 | 124.545 | 127.6587 | 203.265 | 134.1214 | 137.4744 | 140.9113 | 144.4341 | 311.9066
2 | Revenues ($1,000's)
a | State Grants | 1156.5451
b | Federal Grants | 693.9271
c | Energy |  | 80.2007 | 82.2057 | 84.2609 | 86.3674 | 88.5266 | 90.7398 | 93.0083 | 95.3335 | 97.7168 | 100.1597 | 102.6637 | 105.2303 | 107.8611 | 110.5576 | 113.3215 | 116.1546 | 119.0584 | 122.0349 | 125.0858 | 128.2129
d | Recs |  | 16.0401 | 16.4411 | 16.8522 | 17.2735 | 17.7053 | 18.148 | 18.6017 | 19.0667 | 19.5434 | 20.0319 | 20.5327 | 21.0461 | 21.5722 | 22.1115 | 22.6643 | 23.2309 | 23.8117 | 24.407 | 25.0172 | 25.6426
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 232.4226
h | Subtotal, Revenues | 1850.4722 | 96.2409 | 98.6469 | 101.1131 | 103.6409 | 106.2319 | 108.8877 | 111.6099 | 114.4001 | 117.2602 | 120.1917 | 123.1964 | 126.2764 | 129.4333 | 132.6691 | 135.9858 | 139.3855 | 142.8701 | 146.4419 | 150.1029 | 386.2781
3790.2677
3 | Cashflows ($1,000's) | [21 empty] | 232.4226
a | Nominal Dollars | -2775.7083 | 3.6347 | 3.7255 | 3.8187 | 3.9141 | -52.5584 | 4.1123 | 4.2151 | 4.3205 | 4.4285 | -123.4692 | 4.6527 | 4.769 | 4.8882 | 5.0104 | -67.2792 | 5.2641 | 5.3957 | 5.5306 | 5.6688 | 74.3715
b | NPV | -2775.7083 | 3.4616 | 3.3792 | 3.2987 | 3.2202 | -41.1809 | 3.0687 | 2.9956 | 2.9243 | 2.8546 | -75.7994 | 2.7203 | 2.6556 | 2.5923 | 2.5306 | -32.3625 | 2.4115 | 2.3541 | 2.2981 | 2.2434 | 28.0299
c | Cum NPV | -2775.7083 | -2772.2467 | -2768.8675 | -2765.5688 | -2762.3486 | -2803.5295 | -2800.4609 | -2797.4653 | -2794.541 | -2791.6864 | -2867.4858 | -2864.7654 | -2862.1099 | -2859.5175 | -2856.9869 | -2889.3494 | -2886.9378 | -2884.5837 | -2882.2857 | -2880.0423 | -2852.0124
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 625.9569 |  | Max KW | 176.278 |  | State Grants | 1156.5451 |  | Fed Grants | 693.9271
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | #DIV/0! |  | Cum NPV | -2852.0124 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma C
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 4720.7116
b | O&M |  | 12.775 | 13.0943 | 13.4217 | 13.7572 | 14.1012 | 14.4537 | 14.815 | 15.1854 | 15.5651 | 15.9542 | 16.353 | 16.7619 | 17.1809 | 17.6104 | 18.0507 | 18.502 | 18.9645 | 19.4386 | 19.9246 | 20.4227
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 12.0968 | 12.3992 | 12.7092 | 13.027 | 13.3526 | 13.6864 | 14.0286 | 14.3793 | 14.7388 | 15.1073 | 15.485 | 15.8721 | 16.2689 | 16.6756 | 17.0925 | 17.5198 | 17.9578 | 18.4067 | 18.8669 | 19.3386
e | Payment in lieu of Property Taxes |  | 72.5809 | 74.3955 | 76.2554 | 78.1617 | 80.1158 | 82.1187 | 84.1716 | 86.2759 | 88.4328 | 90.6436 | 92.9097 | 95.2325 | 97.6133 | 100.0536 | 102.555 | 105.1188 | 107.7468 | 110.4405 | 113.2015 | 116.0315
f
g | Subtotal, Costs | 4720.7116 | 97.4527 | 99.889 | 102.3863 | 104.9459 | 164.14 | 110.2588 | 113.0153 | 115.8407 | 118.7367 | 249.7136 | 124.7477 | 127.8664 | 131.0631 | 134.3397 | 210.1131 | 141.1406 | 144.6691 | 148.2859 | 151.993 | 319.6545
2 | Revenues ($1,000's)
a | State Grants | 1180.1779
b | Federal Grants | 708.1067
c | Energy |  | 106.4581 | 109.1195 | 111.8475 | 114.6437 | 117.5098 | 120.4475 | 123.4587 | 126.5452 | 129.7088 | 132.9515 | 136.2753 | 139.6822 | 143.1743 | 146.7536 | 150.4224 | 154.183 | 158.0376 | 161.9885 | 166.0382 | 170.1892
d | Recs |  | 21.2916 | 21.8239 | 22.3695 | 22.9287 | 23.502 | 24.0895 | 24.6917 | 25.309 | 25.9418 | 26.5903 | 27.2551 | 27.9364 | 28.6349 | 29.3507 | 30.0845 | 30.8366 | 31.6075 | 32.3977 | 33.2076 | 34.0378
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 1937.3682
h | Subtotal, Revenues | 1888.2846 | 127.7497 | 130.9434 | 134.217 | 137.5724 | 141.0117 | 144.537 | 148.1504 | 151.8542 | 155.6506 | 159.5418 | 163.5304 | 167.6186 | 171.8091 | 176.1043 | 180.5069 | 185.0196 | 189.6451 | 194.3862 | 199.2459 | 2141.5952
3867.7178
3 | Cashflows ($1,000's) | [21 empty] | 1937.3682
a | Nominal Dollars | -2832.427 | 30.2969 | 31.0544 | 31.8307 | 32.6265 | -23.1283 | 34.2782 | 35.1352 | 36.0135 | 36.9139 | -90.1717 | 38.7826 | 39.7522 | 40.746 | 41.7647 | -29.6061 | 43.879 | 44.976 | 46.1004 | 47.2529 | 1821.9407
b | NPV | -2832.427 | 28.8542 | 28.1672 | 27.4966 | 26.8419 | -18.1216 | 25.5789 | 24.9699 | 24.3754 | 23.795 | -55.3576 | 22.6754 | 22.1355 | 21.6085 | 21.094 | -14.2411 | 20.1015 | 19.6229 | 19.1557 | 18.6996 | 686.6703
c | Cum NPV | -2832.427 | -2803.5727 | -2775.4055 | -2747.9089 | -2721.067 | -2739.1886 | -2713.6097 | -2688.6398 | -2664.2644 | -2640.4694 | -2695.827 | -2673.1516 | -2651.0161 | -2629.4076 | -2608.3137 | -2622.5547 | -2602.4532 | -2582.8304 | -2563.6747 | -2544.9751 | -1858.3048
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 830.8922 |  | Max KW | 287.6502 |  | State Grants | 1180.1779 |  | Fed Grants | 708.1067
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | -1.156% |  | Cum NPV | -1858.3048 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma C (no min flow)
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 5837.7521
b | O&M |  | 29.0425 | 29.7686 | 30.5128 | 31.2756 | 32.0575 | 32.8589 | 33.6804 | 34.5224 | 35.3855 | 36.2701 | 37.1769 | 38.1063 | 39.059 | 40.0354 | 41.0363 | 42.0622 | 43.1138 | 44.1916 | 45.2964 | 46.4288
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 14.9592 | 15.3332 | 15.7166 | 16.1095 | 16.5122 | 16.925 | 17.3481 | 17.7818 | 18.2264 | 18.682 | 19.1491 | 19.6278 | 20.1185 | 20.6215 | 21.137 | 21.6654 | 22.2071 | 22.7623 | 23.3313 | 23.9146
e | Payment in lieu of Property Taxes |  | 89.7554 | 91.9993 | 94.2993 | 96.6568 | 99.0732 | 101.55 | 104.0888 | 106.691 | 109.3583 | 112.0922 | 114.8946 | 117.7669 | 120.7111 | 123.7289 | 126.8221 | 129.9926 | 133.2425 | 136.5735 | 139.9879 | 143.4875
f
g | Subtotal, Costs | 5837.7521 | 133.7572 | 137.1011 | 140.5287 | 144.0419 | 204.2133 | 151.334 | 155.1173 | 158.9953 | 162.9702 | 295.0529 | 171.2205 | 175.501 | 179.8886 | 184.3858 | 261.4103 | 193.7203 | 198.5633 | 203.5274 | 208.6156 | 377.6926
2 | Revenues ($1,000's)
a | State Grants | 1459.438
b | Federal Grants | 875.6628
c | Energy |  | 242.021 | 248.0715 | 254.2733 | 260.6301 | 267.1459 | 273.8245 | 280.6701 | 287.6869 | 294.8791 | 302.251 | 309.8073 | 317.5525 | 325.4913 | 333.6286 | 341.9693 | 350.5185 | 359.2815 | 368.2635 | 377.4701 | 386.9069
d | Recs |  | 48.4042 | 49.6143 | 50.8547 | 52.126 | 53.4292 | 54.7649 | 56.134 | 57.5374 | 58.9758 | 60.4502 | 61.9615 | 63.5105 | 65.0983 | 66.7257 | 68.3939 | 70.1037 | 71.8563 | 73.6527 | 75.494 | 77.3814
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 10018.2915
h | Subtotal, Revenues | 2335.1009 | 290.4252 | 297.6858 | 305.1279 | 312.7561 | 320.575 | 328.5894 | 336.8042 | 345.2243 | 353.8549 | 362.7012 | 371.7688 | 381.063 | 390.5896 | 400.3543 | 410.3632 | 420.6222 | 431.1378 | 441.9162 | 452.9642 | 10482.5798
4782.9183
3 | Cashflows ($1,000's) | [21 empty] | 10018.2915
a | Nominal Dollars | -3502.6513 | 156.668 | 160.5847 | 164.5993 | 168.7143 | 116.3617 | 177.2554 | 181.6868 | 186.229 | 190.8847 | 67.6484 | 200.5483 | 205.562 | 210.701 | 215.9685 | 148.9528 | 226.9019 | 232.5745 | 238.3889 | 244.3486 | 10104.8872
b | NPV | -3502.6513 | 149.2076 | 145.655 | 142.1871 | 138.8017 | 91.1725 | 132.2707 | 129.1214 | 126.0471 | 123.046 | 41.5302 | 117.2564 | 114.4646 | 111.7392 | 109.0788 | 71.6489 | 103.9464 | 101.4715 | 99.0555 | 96.697 | 3808.4257
c | Cum NPV | -3502.6513 | -3353.4437 | -3207.7886 | -3065.6016 | -2926.7999 | -2835.6275 | -2703.3568 | -2574.2353 | -2448.1882 | -2325.1422 | -2283.612 | -2166.3556 | -2051.891 | -1940.1517 | -1831.073 | -1759.4241 | -1655.4777 | -1554.0062 | -1454.9507 | -1358.2537 | 2450.172
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 1888.9442 |  | Max KW | 533.6683 |  | State Grants | 1459.438 |  | Fed Grants | 875.6628
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | 8.674% |  | Cum NPV | 2450.172 |  |  |  |  | Discounted Pay Back | 19
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma C (1-2 min flow)
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 4976.0082
b | O&M |  | 17.4886 | 17.9258 | 18.3739 | 18.8333 | 19.3041 | 19.7867 | 20.2814 | 20.7884 | 21.3081 | 21.8408 | 22.3868 | 22.9465 | 23.5202 | 24.1082 | 24.7109 | 25.3287 | 25.9619 | 26.6109 | 27.2762 | 27.9581
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 12.751 | 13.0698 | 13.3965 | 13.7315 | 14.0747 | 14.4266 | 14.7873 | 15.157 | 15.5359 | 15.9243 | 16.3224 | 16.7304 | 17.1487 | 17.5774 | 18.0169 | 18.4673 | 18.929 | 19.4022 | 19.8872 | 20.3844
e | Payment in lieu of Property Taxes |  | 76.5061 | 78.4188 | 80.3792 | 82.3887 | 84.4484 | 86.5597 | 88.7237 | 90.9417 | 93.2153 | 95.5457 | 97.9343 | 100.3827 | 102.8922 | 105.4645 | 108.1012 | 110.8037 | 113.5738 | 116.4131 | 119.3234 | 122.3065
f
g | Subtotal, Costs | 4976.0082 | 106.7457 | 109.4144 | 112.1497 | 114.9535 | 174.3977 | 120.773 | 123.7923 | 126.8871 | 130.0593 | 261.3192 | 136.6435 | 140.0596 | 143.5611 | 147.1502 | 223.2438 | 154.5996 | 158.4646 | 162.4262 | 166.4869 | 334.5107
2 | Revenues ($1,000's)
a | State Grants | 1244.0021
b | Federal Grants | 708.1067
c | Energy |  | 145.7381 | 149.3815 | 153.1161 | 156.944 | 160.8676 | 164.8893 | 169.0115 | 173.2368 | 177.5677 | 182.0069 | 186.5571 | 191.221 | 196.0015 | 200.9016 | 205.9241 | 211.0722 | 216.349 | 221.7577 | 227.3017 | 232.9842
d | Recs |  | 29.1476 | 29.8763 | 30.6232 | 31.3888 | 32.1735 | 32.9779 | 33.8023 | 34.6474 | 35.5135 | 36.4014 | 37.3114 | 38.2442 | 39.2003 | 40.1803 | 41.1848 | 42.2144 | 43.2698 | 44.3515 | 45.4603 | 46.5968
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 4357.2801
h | Subtotal, Revenues | 1952.1088 | 174.8857 | 179.2578 | 183.7393 | 188.3328 | 193.0411 | 197.8671 | 202.8138 | 207.8841 | 213.0812 | 218.4083 | 223.8685 | 229.4652 | 235.2018 | 241.0819 | 247.1089 | 253.2866 | 259.6188 | 266.1093 | 272.762 | 4636.8612
4076.8844
3 | Cashflows ($1,000's) | [21 empty] | 4357.2801
a | Nominal Dollars | -3023.8994 | 68.14 | 69.8435 | 71.5896 | 73.3793 | 18.6434 | 77.0941 | 79.0215 | 80.997 | 83.022 | -42.9109 | 87.2249 | 89.4056 | 91.6407 | 93.9317 | 23.8651 | 98.687 | 101.1542 | 103.683 | 106.2751 | 4302.3505
b | NPV | -3023.8994 | 64.8952 | 63.3501 | 61.8418 | 60.3693 | 14.6076 | 57.5288 | 56.1591 | 54.822 | 53.5167 | -26.3436 | 50.9986 | 49.7844 | 48.599 | 47.4419 | 11.4795 | 45.2097 | 44.1332 | 43.0824 | 42.0567 | 1621.5106
c | Cum NPV | -3023.8994 | -2959.0042 | -2895.6541 | -2833.8123 | -2773.443 | -2758.8354 | -2701.3066 | -2645.1475 | -2590.3255 | -2536.8088 | -2563.1524 | -2512.1538 | -2462.3694 | -2413.7704 | -2366.3285 | -2354.849 | -2309.6393 | -2265.5061 | -2222.4236 | -2180.3669 | -558.8563
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 1137.468 |  | Max KW | 326.4159 |  | State Grants | 1244.0021 |  | Fed Grants | 708.1067
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | 3.71% |  | Cum NPV | -558.8563 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma C-2
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 4211.9854
b | O&M |  | 11.4168 | 11.7023 | 11.9948 | 12.2947 | 12.6021 | 12.9171 | 13.24 | 13.571 | 13.9103 | 14.2581 | 14.6145 | 14.9799 | 15.3544 | 15.7382 | 16.1317 | 16.535 | 16.9484 | 17.3721 | 17.8064 | 18.2515
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 10.7932 | 11.063 | 11.3396 | 11.6231 | 11.9137 | 12.2115 | 12.5168 | 12.8297 | 13.1505 | 13.4792 | 13.8162 | 14.1616 | 14.5157 | 14.8786 | 15.2505 | 15.6318 | 16.0226 | 16.4231 | 16.8337 | 17.2546
e | Payment in lieu of Property Taxes |  | 64.7593 | 66.3783 | 68.0377 | 69.7387 | 71.4821 | 73.2692 | 75.1009 | 76.9784 | 78.9029 | 80.8755 | 82.8973 | 84.9698 | 87.094 | 89.2714 | 91.5032 | 93.7907 | 96.1355 | 98.5389 | 101.0024 | 103.5274
f
g | Subtotal, Costs | 4211.9854 | 86.9693 | 89.1436 | 91.3722 | 93.6565 | 152.5683 | 98.3978 | 100.8578 | 103.3792 | 105.9637 | 236.6212 | 111.3281 | 114.1113 | 116.9641 | 119.8882 | 195.3003 | 125.9575 | 129.1065 | 132.3341 | 135.6425 | 302.8952
2 | Revenues ($1,000's)
a | State Grants | 1052.9963
b | Federal Grants | 631.7978
c | Energy |  | 95.1403 | 97.5189 | 99.9568 | 102.4557 | 105.0171 | 107.6426 | 110.3336 | 113.092 | 115.9193 | 118.8173 | 121.7877 | 124.8324 | 127.9532 | 131.152 | 134.4308 | 137.7916 | 141.2364 | 144.7673 | 148.3865 | 152.0961
d | Recs |  | 19.0281 | 19.5038 | 19.9914 | 20.4911 | 21.0034 | 21.5285 | 22.0667 | 22.6184 | 23.1839 | 23.7635 | 24.3575 | 24.9665 | 25.5906 | 26.2304 | 26.8862 | 27.5583 | 28.2473 | 28.9535 | 29.6773 | 30.4192
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 1739.2731
h | Subtotal, Revenues | 1684.7942 | 114.1684 | 117.0226 | 119.9482 | 122.9469 | 126.0206 | 129.1711 | 132.4004 | 135.7104 | 139.1031 | 142.5807 | 146.1452 | 149.7989 | 153.5438 | 157.3824 | 161.317 | 165.3499 | 169.4837 | 173.7208 | 178.0638 | 1921.7885
3450.9143
3 | Cashflows ($1,000's) | [21 empty] | 1739.2731
a | Nominal Dollars | -2527.1912 | 27.1991 | 27.8791 | 28.576 | 29.2904 | -26.5477 | 30.7733 | 31.5426 | 32.3312 | 33.1394 | -94.0405 | 34.8171 | 35.6876 | 36.5798 | 37.4942 | -33.9833 | 39.3924 | 40.3772 | 41.3866 | 42.4213 | 1618.8933
b | NPV | -2527.1912 | 25.9039 | 25.2871 | 24.6851 | 24.0973 | -20.8008 | 22.9635 | 22.4167 | 21.883 | 21.362 | -57.7327 | 20.3569 | 19.8722 | 19.399 | 18.9371 | -16.3466 | 18.0461 | 17.6164 | 17.197 | 16.7875 | 610.1439
c | Cum NPV | -2527.1912 | -2501.2873 | -2476.0002 | -2451.3151 | -2427.2178 | -2448.0186 | -2425.0552 | -2402.6384 | -2380.7554 | -2359.3934 | -2417.1261 | -2396.7693 | -2376.8971 | -2357.4981 | -2338.561 | -2354.9075 | -2336.8614 | -2319.245 | -2302.048 | -2285.2604 | -1675.1166
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 742.5588 |  | Max KW | 282.2584 |  | State Grants | 1052.9963 |  | Fed Grants | 631.7978
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | -1.231% |  | Cum NPV | -1675.1166 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma D
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 3363.7447
b | O&M |  | 6.1506 | 6.3044 | 6.462 | 6.6235 | 6.7891 | 6.9588 | 7.1328 | 7.3111 | 7.4939 | 7.6812 | 7.8733 | 8.0701 | 8.2719 | 8.4787 | 8.6906 | 8.9079 | 9.1306 | 9.3588 | 9.5928 | 9.8326
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 8.6196 | 8.8351 | 9.056 | 9.2824 | 9.5144 | 9.7523 | 9.9961 | 10.246 | 10.5021 | 10.7647 | 11.0338 | 11.3097 | 11.5924 | 11.8822 | 12.1793 | 12.4837 | 12.7958 | 13.1157 | 13.4436 | 13.7797
e | Payment in lieu of Property Taxes |  | 51.7176 | 53.0105 | 54.3358 | 55.6942 | 57.0865 | 58.5137 | 59.9765 | 61.4759 | 63.0128 | 64.5882 | 66.2029 | 67.8579 | 69.5544 | 71.2932 | 73.0756 | 74.9025 | 76.775 | 78.6944 | 80.6618 | 82.6783
f
g | Subtotal, Costs | 3363.7447 | 66.4878 | 68.15 | 69.8537 | 71.6 | 129.9605 | 75.2248 | 77.1054 | 79.0331 | 81.0089 | 211.0426 | 85.11 | 87.2377 | 89.4186 | 91.6541 | 166.3604 | 96.2941 | 98.7015 | 101.169 | 103.6982 | 270.1523
2 | Revenues ($1,000's)
a | State Grants | 840.9362
b | Federal Grants | 504.5617
c | Energy |  | 51.2549 | 52.5363 | 53.8497 | 55.1959 | 56.5758 | 57.9902 | 59.44 | 60.926 | 62.4491 | 64.0104 | 65.6106 | 67.2509 | 68.9322 | 70.6555 | 72.4218 | 74.2324 | 76.0882 | 77.9904 | 79.9402 | 81.9387
d | Recs |  | 10.251 | 10.5073 | 10.7699 | 11.0392 | 11.3152 | 11.598 | 11.888 | 12.1852 | 12.4898 | 12.8021 | 13.1221 | 13.4502 | 13.7864 | 14.1311 | 14.4844 | 14.8465 | 15.2176 | 15.5981 | 15.988 | 16.3877
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 0
h | Subtotal, Revenues | 1345.4979 | 61.5059 | 63.0435 | 64.6196 | 66.2351 | 67.891 | 69.5883 | 71.328 | 73.1112 | 74.939 | 76.8124 | 78.7327 | 80.7011 | 82.7186 | 84.7866 | 86.9062 | 89.0789 | 91.3058 | 93.5885 | 95.9282 | 98.3264
2755.9437
3 | Cashflows ($1,000's) | [21 empty] | -318.5705
a | Nominal Dollars | -2018.2468 | -4.9819 | -5.1064 | -5.2341 | -5.3649 | -62.0695 | -5.6365 | -5.7774 | -5.9219 | -6.0699 | -134.2301 | -6.3772 | -6.5366 | -6.7001 | -6.8676 | -79.4542 | -7.2152 | -7.3956 | -7.5805 | -7.77 | -171.8259
b | NPV | -2018.2468 | -4.7446 | -4.6317 | -4.5214 | -4.4137 | -48.633 | -4.2061 | -4.1059 | -4.0082 | -3.9127 | -82.4057 | -3.7286 | -3.6398 | -3.5532 | -3.4686 | -38.2188 | -3.3054 | -3.2267 | -3.1499 | -3.0749 | -64.7594
c | Cum NPV | -2018.2468 | -2022.9914 | -2027.6231 | -2032.1445 | -2036.5582 | -2085.1913 | -2089.3973 | -2093.5033 | -2097.5114 | -2101.4241 | -2183.8298 | -2187.5584 | -2191.1983 | -2194.7514 | -2198.22 | -2236.4388 | -2239.7442 | -2242.9709 | -2246.1207 | -2249.1956 | -2313.955
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 400.0383 |  | Max KW | 111.6471 |  | State Grants | 840.9362 |  | Fed Grants | 504.5617
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | #DIV/0! |  | Cum NPV | -2313.955 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma E
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 3325.6498
b | O&M |  | 8.0592 | 8.2607 | 8.4672 | 8.6789 | 8.8959 | 9.1183 | 9.3462 | 9.5799 | 9.8194 | 10.0649 | 10.3165 | 10.5744 | 10.8388 | 11.1097 | 11.3875 | 11.6722 | 11.964 | 12.2631 | 12.5696 | 12.8839
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 8.522 | 8.735 | 8.9534 | 9.1772 | 9.4067 | 9.6418 | 9.8829 | 10.13 | 10.3832 | 10.6428 | 10.9089 | 11.1816 | 11.4611 | 11.7476 | 12.0413 | 12.3424 | 12.6509 | 12.9672 | 13.2914 | 13.6237
e | Payment in lieu of Property Taxes |  | 51.1319 | 52.4102 | 53.7204 | 55.0634 | 56.44 | 57.851 | 59.2973 | 60.7797 | 62.2992 | 63.8567 | 65.4531 | 67.0894 | 68.7667 | 70.4858 | 72.248 | 74.0542 | 75.9055 | 77.8032 | 79.7483 | 81.742
f
g | Subtotal, Costs | 3325.6498 | 67.7131 | 69.4059 | 71.141 | 72.9196 | 131.313 | 76.6111 | 78.5264 | 80.4896 | 82.5018 | 212.5728 | 86.6784 | 88.8454 | 91.0665 | 93.3432 | 168.0917 | 98.0687 | 100.5204 | 103.0334 | 105.6093 | 272.1111
2 | Revenues ($1,000's)
a | State Grants | 831.4125
b | Federal Grants | 498.8475
c | Energy |  | 67.1602 | 68.8392 | 70.5601 | 72.3241 | 74.1322 | 75.9856 | 77.8852 | 79.8323 | 81.8281 | 83.8738 | 85.9707 | 88.1199 | 90.3229 | 92.581 | 94.8955 | 97.2679 | 99.6996 | 102.1921 | 104.7469 | 107.3656
d | Recs |  | 13.432 | 13.7678 | 14.112 | 14.4648 | 14.8264 | 15.1971 | 15.577 | 15.9665 | 16.3656 | 16.7748 | 17.1941 | 17.624 | 18.0646 | 18.5162 | 18.9791 | 19.4536 | 19.9399 | 20.4384 | 20.9494 | 21.4731
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 823.5685
h | Subtotal, Revenues | 1330.2599 | 80.5922 | 82.607 | 84.6722 | 86.789 | 88.9587 | 91.1827 | 93.4622 | 95.7988 | 98.1938 | 100.6486 | 103.1648 | 105.7439 | 108.3875 | 111.0972 | 113.8746 | 116.7215 | 119.6396 | 122.6305 | 125.6963 | 952.4073
2724.7322
3 | Cashflows ($1,000's) | [21 empty] | 823.5685
a | Nominal Dollars | -1995.3899 | 12.8791 | 13.2011 | 13.5311 | 13.8694 | -42.3543 | 14.5715 | 14.9358 | 15.3092 | 15.692 | -111.9242 | 16.4864 | 16.8985 | 17.321 | 17.754 | -54.217 | 18.6528 | 19.1191 | 19.5971 | 20.087 | 680.2961
b | NPV | -1995.3899 | 12.2658 | 11.9738 | 11.6887 | 11.4104 | -33.1857 | 10.8735 | 10.6146 | 10.3619 | 10.1152 | -68.7117 | 9.6392 | 9.4097 | 9.1857 | 8.967 | -26.0793 | 8.5451 | 8.3416 | 8.143 | 7.9491 | 256.3965
c | Cum NPV | -1995.3899 | -1983.124 | -1971.1503 | -1959.4616 | -1948.0512 | -1981.2368 | -1970.3633 | -1959.7487 | -1949.3868 | -1939.2716 | -2007.9834 | -1998.3442 | -1988.9344 | -1979.7487 | -1970.7817 | -1996.8611 | -1988.316 | -1979.9744 | -1971.8314 | -1963.8823 | -1707.4858
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 524.1768 |  | Max KW | 184.0843 |  | State Grants | 831.4125 |  | Fed Grants | 498.8475
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | #NUM! |  | Cum NPV | -1707.4858 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma E (no min flow)
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 4019.7894
b | O&M |  | 18.2113 | 18.6666 | 19.1333 | 19.6116 | 20.1019 | 20.6044 | 21.1195 | 21.6475 | 22.1887 | 22.7434 | 23.312 | 23.8948 | 24.4922 | 25.1045 | 25.7321 | 26.3754 | 27.0348 | 27.7107 | 28.4034 | 29.1135
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 10.3007 | 10.5582 | 10.8222 | 11.0927 | 11.3701 | 11.6543 | 11.9457 | 12.2443 | 12.5504 | 12.8642 | 13.1858 | 13.5154 | 13.8533 | 14.1996 | 14.5546 | 14.9185 | 15.2915 | 15.6737 | 16.0656 | 16.4672
e | Payment in lieu of Property Taxes |  | 61.8043 | 63.3494 | 64.9331 | 66.5564 | 68.2203 | 69.9258 | 71.674 | 73.4658 | 75.3025 | 77.1851 | 79.1147 | 81.0925 | 83.1199 | 85.1979 | 87.3278 | 89.511 | 91.7488 | 94.0425 | 96.3936 | 98.8034
f
g | Subtotal, Costs | 4019.7894 | 90.3163 | 92.5742 | 94.8886 | 97.2608 | 156.2627 | 102.1846 | 104.7392 | 107.3577 | 110.0416 | 240.8011 | 115.6125 | 118.5028 | 121.4654 | 124.502 | 200.0295 | 130.8049 | 134.075 | 137.4269 | 140.8626 | 308.2458
2 | Revenues ($1,000's)
a | State Grants | 1004.9474
b | Federal Grants | 602.9684
c | Energy |  | 151.761 | 155.555 | 159.4439 | 163.43 | 167.5158 | 171.7037 | 175.9962 | 180.3961 | 184.9061 | 189.5287 | 194.2669 | 199.1236 | 204.1017 | 209.2042 | 214.4343 | 219.7952 | 225.2901 | 230.9223 | 236.6954 | 242.6128
d | Recs |  | 30.3522 | 31.111 | 31.8888 | 32.686 | 33.5032 | 34.3407 | 35.1992 | 36.0792 | 36.9812 | 37.9057 | 38.8534 | 39.8247 | 40.8203 | 41.8408 | 42.8869 | 43.959 | 45.058 | 46.1845 | 47.3391 | 48.5226
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 5870.0464
h | Subtotal, Revenues | 1607.9158 | 182.1132 | 186.666 | 191.3327 | 196.116 | 201.0189 | 206.0444 | 211.1955 | 216.4754 | 221.8873 | 227.4344 | 233.1203 | 238.9483 | 244.922 | 251.0451 | 257.3212 | 263.7542 | 270.3481 | 277.1068 | 284.0345 | 6161.1817
3293.4465
3 | Cashflows ($1,000's) | [21 empty] | 5870.0464
a | Nominal Dollars | -2411.8736 | 91.7969 | 94.0918 | 96.4441 | 98.8552 | 44.7562 | 103.8598 | 106.4563 | 109.1177 | 111.8456 | -13.3667 | 117.5078 | 120.4455 | 123.4566 | 126.5431 | 57.2917 | 132.9493 | 136.273 | 139.6799 | 143.1719 | 5852.9359
b | NPV | -2411.8736 | 87.4256 | 85.3441 | 83.3121 | 81.3285 | 35.0677 | 77.5018 | 75.6565 | 73.8551 | 72.0967 | -8.206 | 68.7044 | 67.0686 | 65.4717 | 63.9128 | 27.5583 | 60.9056 | 59.4555 | 58.0399 | 56.658 | 2205.91
c | Cum NPV | -2411.8736 | -2324.448 | -2239.1039 | -2155.7919 | -2074.4634 | -2039.3957 | -1961.894 | -1886.2375 | -1812.3823 | -1740.2856 | -1748.4916 | -1679.7872 | -1612.7187 | -1547.247 | -1483.3341 | -1455.7758 | -1394.8702 | -1335.4147 | -1277.3749 | -1220.7169 | 985.1931
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 1184.4762 |  | Max KW | 340.7352 |  | State Grants | 1004.9474 |  | Fed Grants | 602.9684
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | 7.303% |  | Cum NPV | 985.1931 |  |  |  |  | Discounted Pay Back | 19
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma E (1-2 min flow)
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 3519.012
b | O&M |  | 11.0249 | 11.3005 | 11.5831 | 11.8726 | 12.1694 | 12.4737 | 12.7855 | 13.1052 | 13.4328 | 13.7686 | 14.1128 | 14.4656 | 14.8273 | 15.198 | 15.5779 | 15.9674 | 16.3666 | 16.7757 | 17.1951 | 17.625
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 9.0175 | 9.2429 | 9.474 | 9.7108 | 9.9536 | 10.2024 | 10.4575 | 10.7189 | 10.9869 | 11.2616 | 11.5431 | 11.8317 | 12.1275 | 12.4307 | 12.7414 | 13.06 | 13.3865 | 13.7211 | 14.0642 | 14.4158
e | Payment in lieu of Property Taxes |  | 54.1048 | 55.4574 | 56.8439 | 58.265 | 59.7216 | 61.2146 | 62.745 | 64.3136 | 65.9215 | 67.5695 | 69.2587 | 70.9902 | 72.765 | 74.5841 | 76.4487 | 78.3599 | 80.3189 | 82.3269 | 84.385 | 86.4947
f
g | Subtotal, Costs | 3519.012 | 74.1472 | 76.0009 | 77.9009 | 79.8484 | 138.415 | 83.8907 | 85.988 | 88.1377 | 90.3412 | 220.6081 | 94.9147 | 97.2875 | 99.7197 | 102.2127 | 177.183 | 107.3872 | 110.0719 | 112.8237 | 115.6443 | 282.3971
2 | Revenues ($1,000's)
a | State Grants | 879.753
b | Federal Grants | 527.8518
c | Energy |  | 91.8743 | 94.1712 | 96.5254 | 98.9386 | 101.4121 | 103.9474 | 106.546 | 109.2097 | 111.9399 | 114.7384 | 117.6069 | 120.5471 | 123.5607 | 126.6498 | 129.816 | 133.0614 | 136.3879 | 139.7976 | 143.2926 | 146.8749
d | Recs |  | 18.3749 | 18.8342 | 19.3051 | 19.7877 | 20.2824 | 20.7895 | 21.3092 | 21.8419 | 22.388 | 22.9477 | 23.5214 | 24.1094 | 24.7121 | 25.33 | 25.9632 | 26.6123 | 27.2776 | 27.9595 | 28.6585 | 29.375
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 2308.5775
h | Subtotal, Revenues | 1407.6048 | 110.2492 | 113.0054 | 115.8305 | 118.7263 | 121.6945 | 124.7368 | 127.8552 | 131.0516 | 134.3279 | 137.6861 | 141.1283 | 144.6565 | 148.2729 | 151.9797 | 155.7792 | 159.6737 | 163.6655 | 167.7572 | 171.9511 | 2484.8274
2883.1554
3 | Cashflows ($1,000's) | [21 empty] | 2308.5775
a | Nominal Dollars | -2111.4072 | 36.102 | 37.0045 | 37.9296 | 38.8779 | -16.7206 | 40.8461 | 41.8672 | 42.9139 | 43.9868 | -82.922 | 46.2136 | 47.3689 | 48.5531 | 49.767 | -21.4038 | 52.2864 | 53.5936 | 54.9334 | 56.3068 | 2202.4303
b | NPV | -2111.4072 | 34.3828 | 33.5642 | 32.7651 | 31.9849 | -13.101 | 30.48 | 29.7543 | 29.0458 | 28.3543 | -50.9069 | 27.0201 | 26.3768 | 25.7488 | 25.1357 | -10.2956 | 23.953 | 23.3827 | 22.826 | 22.2825 | 830.0728
c | Cum NPV | -2111.4072 | -2077.0244 | -2043.4602 | -2010.6951 | -1978.7102 | -1991.8112 | -1961.3312 | -1931.577 | -1902.5311 | -1874.1769 | -1925.0838 | -1898.0637 | -1871.6869 | -1845.9381 | -1820.8024 | -1831.098 | -1807.145 | -1783.7623 | -1760.9363 | -1738.6538 | -908.581
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 717.0678 |  | Max KW | 208.6515 |  | State Grants | 879.753 |  | Fed Grants | 527.8518
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | 1.614% |  | Cum NPV | -908.581 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma E-2
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 2836.3636
b | O&M |  | 7.1329 | 7.3112 | 7.494 | 7.6814 | 7.8734 | 8.0702 | 8.272 | 8.4788 | 8.6907 | 8.908 | 9.1307 | 9.359 | 9.593 | 9.8328 | 10.0786 | 10.3306 | 10.5888 | 10.8536 | 11.1249 | 11.403
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 7.2682 | 7.4499 | 7.6361 | 7.827 | 8.0227 | 8.2233 | 8.4289 | 8.6396 | 8.8556 | 9.077 | 9.3039 | 9.5365 | 9.7749 | 10.0193 | 10.2698 | 10.5265 | 10.7897 | 11.0594 | 11.3359 | 11.6193
e | Payment in lieu of Property Taxes |  | 43.6091 | 44.6993 | 45.8168 | 46.9622 | 48.1363 | 49.3397 | 50.5732 | 51.8375 | 53.1334 | 54.4618 | 55.8233 | 57.2189 | 58.6494 | 60.1156 | 61.6185 | 63.159 | 64.7379 | 66.3564 | 68.0153 | 69.7157
f
g | Subtotal, Costs | 2836.3636 | 58.0102 | 59.4604 | 60.9469 | 62.4706 | 120.6028 | 65.6332 | 67.274 | 68.9559 | 70.6798 | 200.4552 | 74.2579 | 76.1144 | 78.0172 | 79.9677 | 154.3818 | 84.016 | 86.1164 | 88.2693 | 90.4761 | 256.5996
2 | Revenues ($1,000's)
a | State Grants | 709.0909
b | Federal Grants | 425.4545
c | Energy |  | 59.4408 | 60.9269 | 62.45 | 64.0113 | 65.6116 | 67.2519 | 68.9332 | 70.6565 | 72.4229 | 74.2335 | 76.0893 | 77.9915 | 79.9413 | 81.9399 | 83.9884 | 86.0881 | 88.2403 | 90.4463 | 92.7074 | 95.0251
d | Recs |  | 11.8882 | 12.1854 | 12.49 | 12.8023 | 13.1223 | 13.4504 | 13.7866 | 14.1313 | 14.4846 | 14.8467 | 15.2179 | 15.5983 | 15.9883 | 16.388 | 16.7977 | 17.2176 | 17.6481 | 18.0893 | 18.5415 | 19.005
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 851.687
h | Subtotal, Revenues | 1134.5454 | 71.329 | 73.1122 | 74.9401 | 76.8136 | 78.7339 | 80.7022 | 82.7198 | 84.7878 | 86.9075 | 89.0802 | 91.3072 | 93.5899 | 95.9296 | 98.3278 | 100.786 | 103.3057 | 105.8883 | 108.5355 | 111.2489 | 965.7172
2323.856
3 | Cashflows ($1,000's) | [21 empty] | 851.687
a | Nominal Dollars | -1701.8182 | 13.3188 | 13.6518 | 13.9931 | 14.3429 | -41.8689 | 15.0691 | 15.4458 | 15.8319 | 16.2277 | -111.375 | 17.0492 | 17.4755 | 17.9124 | 18.3602 | -53.5957 | 19.2897 | 19.7719 | 20.2662 | 20.7729 | 709.1176
b | NPV | -1701.8182 | 12.6846 | 12.3826 | 12.0878 | 11.8 | -32.8054 | 11.2448 | 10.977 | 10.7157 | 10.4605 | -68.3746 | 9.9683 | 9.731 | 9.4993 | 9.2731 | -25.7805 | 8.8368 | 8.6264 | 8.421 | 8.2205 | 267.2589
c | Cum NPV | -1701.8182 | -1689.1335 | -1676.7509 | -1664.6632 | -1652.8632 | -1685.6686 | -1674.4238 | -1663.4468 | -1652.7311 | -1642.2706 | -1710.6452 | -1700.6769 | -1690.9458 | -1681.4465 | -1672.1734 | -1697.9539 | -1689.117 | -1680.4906 | -1672.0696 | -1663.8491 | -1396.5901
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 463.9286 |  | Max KW | 178.0491 |  | State Grants | 709.0909 |  | Fed Grants | 425.4545
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | #NUM! |  | Cum NPV | -1396.5901 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma E-2 (no min flow)
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 2994.3648
b | O&M |  | 12.5251 | 12.8382 | 13.1592 | 13.4881 | 13.8253 | 14.171 | 14.5253 | 14.8884 | 15.2606 | 15.6421 | 16.0332 | 16.434 | 16.8448 | 17.266 | 17.6976 | 18.1401 | 18.5936 | 19.0584 | 19.5349 | 20.0232
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 7.6731 | 7.8649 | 8.0615 | 8.263 | 8.4696 | 8.6814 | 8.8984 | 9.1209 | 9.3489 | 9.5826 | 9.8222 | 10.0677 | 10.3194 | 10.5774 | 10.8418 | 11.1129 | 11.3907 | 11.6755 | 11.9674 | 12.2665
e | Payment in lieu of Property Taxes |  | 46.0384 | 47.1893 | 48.3691 | 49.5783 | 50.8177 | 52.0882 | 53.3904 | 54.7251 | 56.0933 | 57.4956 | 58.933 | 60.4063 | 61.9165 | 63.4644 | 65.051 | 66.6773 | 68.3442 | 70.0528 | 71.8041 | 73.5992
f
g | Subtotal, Costs | 2994.3648 | 66.2365 | 67.8924 | 69.5897 | 71.3295 | 129.6831 | 74.9405 | 76.814 | 78.7344 | 80.7027 | 210.7288 | 84.7883 | 86.908 | 89.0807 | 91.3078 | 166.0054 | 95.9302 | 98.3285 | 100.7867 | 103.3063 | 269.7506
2 | Revenues ($1,000's)
a | State Grants | 709.0909
b | Federal Grants | 425.4545
c | Energy |  | 104.3757 | 106.9851 | 109.6597 | 112.4012 | 115.2112 | 118.0915 | 121.0438 | 124.0699 | 127.1717 | 130.351 | 133.6097 | 136.95 | 140.3737 | 143.8831 | 147.4801 | 151.1671 | 154.9463 | 158.82 | 162.7905 | 166.8602
d | Recs |  | 20.8751 | 21.397 | 21.9319 | 22.4802 | 23.0422 | 23.6183 | 24.2088 | 24.814 | 25.4343 | 26.0702 | 26.7219 | 27.39 | 28.0747 | 28.7766 | 29.496 | 30.2334 | 30.9893 | 31.764 | 32.5581 | 33.372
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 3773.7314
h | Subtotal, Revenues | 1134.5454 | 125.2508 | 128.3821 | 131.5917 | 134.8815 | 138.2535 | 141.7098 | 145.2526 | 148.8839 | 152.606 | 156.4211 | 160.3317 | 164.34 | 168.4485 | 172.6597 | 176.9762 | 181.4006 | 185.9356 | 190.584 | 195.3486 | 3973.9637
2453.3077
3 | Cashflows ($1,000's) | [21 empty] | 3773.7314
a | Nominal Dollars | -1859.8194 | 59.0143 | 60.4897 | 62.0019 | 63.552 | 8.5704 | 66.7693 | 68.4385 | 70.1495 | 71.9032 | -54.3076 | 75.5433 | 77.4319 | 79.3677 | 81.3519 | 10.9708 | 85.4704 | 87.6071 | 89.7973 | 92.0422 | 3704.2131
b | NPV | -1859.8194 | 56.2041 | 54.8659 | 53.5596 | 52.2844 | 6.7151 | 49.8243 | 48.638 | 47.4799 | 46.3495 | -33.3402 | 44.1686 | 43.117 | 42.0904 | 41.0882 | 5.2771 | 39.155 | 38.2227 | 37.3126 | 36.4242 | 1396.079
c | Cum NPV | -1859.8194 | -1803.6152 | -1748.7493 | -1695.1897 | -1642.9053 | -1636.1902 | -1586.3659 | -1537.7279 | -1490.248 | -1443.8985 | -1477.2387 | -1433.07 | -1389.953 | -1347.8626 | -1306.7744 | -1301.4972 | -1262.3423 | -1224.1196 | -1186.807 | -1150.3827 | 245.6962
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 814.6396 |  | Max KW | 270.634 |  | State Grants | 709.0909 |  | Fed Grants | 425.4545
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | 5.807% |  | Cum NPV | 245.6962 |  |  |  |  | Discounted Pay Back | 19
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma E-3
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 2703.3432
b | O&M |  | 5.1482 | 5.2769 | 5.4088 | 5.544 | 5.6826 | 5.8247 | 5.9703 | 6.1195 | 6.2725 | 6.4293 | 6.5901 | 6.7548 | 6.9237 | 7.0968 | 7.2742 | 7.4561 | 7.6425 | 7.8335 | 8.0294 | 8.2301
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 6.9273 | 7.1005 | 7.278 | 7.46 | 7.6465 | 7.8376 | 8.0336 | 8.2344 | 8.4403 | 8.6513 | 8.8676 | 9.0892 | 9.3165 | 9.5494 | 9.7881 | 10.0328 | 10.2836 | 10.5407 | 10.8043 | 11.0744
e | Payment in lieu of Property Taxes |  | 41.5639 | 42.603 | 43.6681 | 44.7598 | 45.8788 | 47.0257 | 48.2014 | 49.4064 | 50.6416 | 51.9076 | 53.2053 | 54.5354 | 55.8988 | 57.2963 | 58.7287 | 60.1969 | 61.7018 | 63.2444 | 64.8255 | 66.4461
f
g | Subtotal, Costs | 2703.3432 | 53.6394 | 54.9804 | 56.3549 | 57.7637 | 115.7782 | 60.688 | 62.2052 | 63.7604 | 65.3544 | 194.9967 | 68.6629 | 70.3795 | 72.139 | 73.9425 | 148.2059 | 77.6858 | 79.628 | 81.6187 | 83.6591 | 249.6122
2 | Revenues ($1,000's)
a | State Grants | 675.8358
b | Federal Grants | 405.5015
c | Energy |  | 42.9013 | 43.9739 | 45.0732 | 46.2 | 47.355 | 48.5389 | 49.7524 | 50.9962 | 52.2711 | 53.5779 | 54.9173 | 56.2903 | 57.6975 | 59.14 | 60.6185 | 62.1339 | 63.6873 | 65.2794 | 66.9114 | 68.5842
d | Recs |  | 8.5803 | 8.7948 | 9.0146 | 9.24 | 9.471 | 9.7078 | 9.9505 | 10.1992 | 10.4542 | 10.7156 | 10.9835 | 11.2581 | 11.5395 | 11.828 | 12.1237 | 12.4268 | 12.7375 | 13.0559 | 13.3823 | 13.7168
e | Avoided Distribution
f | Capacity/Demand |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
g | Residual Value | [20 empty] | 0
h | Subtotal, Revenues | 1081.3373 | 51.4816 | 52.7686 | 54.0878 | 55.44 | 56.826 | 58.2467 | 59.7029 | 61.1954 | 62.7253 | 64.2935 | 65.9008 | 67.5483 | 69.237 | 70.9679 | 72.7421 | 74.5607 | 76.4247 | 78.3353 | 80.2937 | 82.3011
2214.8713
3 | Cashflows ($1,000's) | [21 empty] | -137.9818
a | Nominal Dollars | -1622.0059 | -2.1578 | -2.2117 | -2.267 | -2.3237 | -58.9522 | -2.4413 | -2.5024 | -2.5649 | -2.6291 | -130.7032 | -2.7621 | -2.8312 | -2.902 | -2.9745 | -75.4638 | -3.1251 | -3.2032 | -3.2833 | -3.3654 | -167.3112
b | NPV | -1622.0059 | -2.055 | -2.0061 | -1.9583 | -1.9117 | -46.1906 | -1.8218 | -1.7784 | -1.736 | -1.6947 | -80.2404 | -1.615 | -1.5765 | -1.539 | -1.5023 | -36.2994 | -1.4317 | -1.3976 | -1.3643 | -1.3318 | -63.0578
c | Cum NPV | -1622.0059 | -1624.061 | -1626.0671 | -1628.0254 | -1629.9371 | -1676.1277 | -1677.9495 | -1679.7279 | -1681.4639 | -1683.1586 | -1763.3991 | -1765.014 | -1766.5906 | -1768.1295 | -1769.6319 | -1805.9313 | -1807.3629 | -1808.7605 | -1810.1248 | -1811.4566 | -1874.5144
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 334.8396 |  | Max KW | 110.0337 |  | State Grants | 675.8358 |  | Fed Grants | 405.5015
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | #DIV/0! |  | Cum NPV | -1874.5144 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Proforma F
No. | Item/ Study Year | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | Notes:
1 | Costs ($1,000's)
a | Initial Investment | 3276.9127
b | O&M |  | 5.7465 | 5.8901 | 6.0374 | 6.1883 | 6.343 | 6.5016 | 6.6641 | 6.8307 | 7.0015 | 7.1766 | 7.356 | 7.5399 | 7.7284 | 7.9216 | 8.1196 | 8.3226 | 8.5307 | 8.7439 | 8.9625 | 9.1866
c | Major Maintenance | [5 empty] | 56.5704 |  |  |  |  | 128.0085 |  |  |  |  | 72.4149 |  |  |  |  | 163.8616
d | Insurance |  | 8.3971 | 8.607 | 8.8222 | 9.0427 | 9.2688 | 9.5005 | 9.738 | 9.9815 | 10.231 | 10.4868 | 10.749 | 11.0177 | 11.2932 | 11.5755 | 11.8649 | 12.1615 | 12.4655 | 12.7772 | 13.0966 | 13.424
e | Payment in lieu of Property Taxes |  | 50.3825 | 51.6421 | 52.9331 | 54.2565 | 55.6129 | 57.0032 | 58.4283 | 59.889 | 61.3862 | 62.9209 | 64.4939 | 66.1062 | 67.7589 | 69.4529 | 71.1892 | 72.9689 | 74.7932 | 76.663 | 78.5796 | 80.544
f
g | Subtotal, Costs | 3276.9127 | 64.5261 | 66.1392 | 67.7927 | 69.4875 | 127.7951 | 73.0053 | 74.8305 | 76.7012 | 78.6188 | 208.5927 | 82.5989 | 84.6638 | 86.7804 | 88.9499 | 163.5886 | 93.453 | 95.7893 | 98.1841 | 100.6387 | 267.0163
2 | Revenues ($1,000's)
a | State Grants | 819.2282
b | Federal Grants | 491.5369
c | Energy |  | 47.8872 | 49.0844 | 50.3115 | 51.5693 | 52.8586 | 54.18 | 55.5345 | 56.9229 | 58.346 | 59.8046 | 61.2997 | 62.8322 | 64.403 | 66.0131 | 67.6634 | 69.355 | 71.0889 | 72.8661 | 74.6878 | 76.555
d | Recs |  | 9.5774 | 9.8169 | 10.0623 | 10.3139 | 10.5717 | 10.836 | 11.1069 | 11.3846 | 11.6692 | 11.9609 | 12.2599 | 12.5664 | 12.8806 | 13.2026 | 13.5327 | 13.871 | 14.2178 | 14.5732 | 14.9376 | 15.311
e | Avoided Distribution
f | Capacity/Demand
g | Residual Value | [20 empty] | 0
h | Subtotal, Revenues | 1310.7651 | 57.4647 | 58.9013 | 60.3738 | 61.8832 | 63.4303 | 65.016 | 66.6414 | 68.3075 | 70.0152 | 71.7655 | 73.5597 | 75.3987 | 77.2836 | 79.2157 | 81.1961 | 83.226 | 85.3067 | 87.4393 | 89.6253 | 91.8659
2684.8015
3 | Cashflows ($1,000's) | [21 empty] | -451.5479
a | Nominal Dollars | -1966.1476 | -7.0614 | -7.2379 | -7.4189 | -7.6043 | -64.3649 | -7.9893 | -8.1891 | -8.3938 | -8.6036 | -136.8272 | -9.0392 | -9.2652 | -9.4968 | -9.7342 | -82.3925 | -10.227 | -10.4827 | -10.7447 | -11.0134 | -175.1503
b | NPV | -1966.1476 | -6.7251 | -6.565 | -6.4087 | -6.2561 | -50.4316 | -5.9618 | -5.8198 | -5.6812 | -5.546 | -84 | -5.285 | -5.1592 | -5.0364 | -4.9164 | -39.6322 | -4.6851 | -4.5736 | -4.4647 | -4.3584 | -66.0123
c | Cum NPV | -1966.1476 | -1972.8727 | -1979.4378 | -1985.8465 | -1992.1026 | -2042.5341 | -2048.4959 | -2054.3157 | -2059.9969 | -2065.5429 | -2149.5429 | -2154.8279 | -2159.9871 | -2165.0235 | -2169.9399 | -2209.5721 | -2214.2572 | -2218.8308 | -2223.2954 | -2227.6538 | -2293.6661
| Proforma Inputs |  | Esc. Rate | 2.5% |  | Disc. Rate | 5% |  | MWH | 373.7541 |  | Max KW | 103.9092 |  | State Grants | 819.2282 |  | Fed Grants | 491.5369
|  |  | Energy Rate | 125 | $/MWH | Avg. Power |  | KW | Rec Rate | 25 | $/MWH | Demand | 0 | $/KW-mos | Distribution |  | $/MWH
| Results |  |  | PreTax, Cash on Cash IRR |  |  | #DIV/0! |  | Cum NPV | -2293.6661 |  |  |  |  | Discounted Pay Back | 20
Assumptions
1 | O&M: 1.5¢/KWH escalated at defined rate (see summary sheet)
2 | Major maintenance: $50k in years 5 & 15, $125k in years 10 & 20 | [10 empty] | Denotes cell input linked to Summary Tab
3 | Payment in Lieu of Property taxes: 1.5% of initial investment, escalated | [10 empty] | Denotes cell input linked to Individual Cost Tabs
4 | Insurance: 0.25% of initial investment, escalated
5 | Residual Value: calculated growth rate of year 19 revenues (only if positive cashflows)

## Costs A
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments | Notes: 12/17/10
1 | General | [5 empty] | Cost Base = Blackstone 3m Pit 9/13/10. Red values and notes indicate changes from base.
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance | Assumes - 261 kw installed 286 cfs hyd cap 14' gross head
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 0.5 | 8000 | 4 | Allowance
d | E&S Control | ft. | 100 | 10 | 1 | Allowance
e | Dam Repairs |  | 1 | 40000 | 40 | From Phase I Dam Repair Costs (MBP Consulting 2010)
f | Subtotal, General |  |  |  | 80
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 677586.0247 | 677.586 | Includes: intake, powerhouse, tailrace and trashrake
i | Structure | cy | 0 | 25 | 0 | From Pawtuxet 1m Pit Costs
ii | Intake | cy | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
iii | Tailrace | cy | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
h | Trashracks | sf | 0 | 400 | 0 | From Pawtuxet 1m Pit. Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Sluice gate |  | 1 | 20000 | 20
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Other |  | 0 |  | 0
q | Subtotal, Powerhouse |  |  |  | 837.586
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 701857.76 | 701.8578 | Runner 1.25m, estimated costs developed from recent projects
b | Shipping Handling & Installation |  | 1 | 163371.552 | 163.3716 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Engineering (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow compliance
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 980.2293
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 20000 | 20 | Allowance
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 0.5 | 60000 | 30 | Allowance
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 77.5
9 | Licensing & Permitting
a | Consultations | year | 2 | 50000 | 100 | Allowance
b | Studies | year | 0.5 | 75000 | 37.5 | Allowance
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 287.5
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 |  | 0
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 20
11 | Interconnection
a | Clear & Grub | acre | 0.5 | 8000 | 4 | Allowance
b | New Line |  | 1 | 33000 | 33 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Includes: sectionalizers, transformers, disconnect switch. From Interconnection Costs (Fostiak Eng. 2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 117
12 | Indirect Costs
a | A/E |  | 1 | 191985.2269 | 191.9852 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 371.9852
Totals
1 | General |  |  |  | 80
2 | Powerhouse/Intake |  |  |  | 837.586
3 | Equipment |  |  |  | 980.2293
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 77.5
9 | Licensing & Permitting |  |  |  | 287.5
10 | Land & Land Rights |  |  |  | 20
11 | Interconnection |  |  |  | 117
| Subtotal, Directs |  |  |  | 2399.8153
12 | Indirect Costs |  |  |  | 371.9852
| Subtotal |  |  |  | 2771.8006
13 | Contingency |  | 2771800.5636 | 20% | 554.3601
| Grand Total |  |  |  | 3326.1607

## Costs B
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments
1 | General
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 8000 | 32 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 90000 | 90 | From Phase I Dam Repair Costs (MBP Consulting 2010)
f | Subtotal, General |  |  |  | 177
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 576263.5453 | 576.2635 | Includes: intake, powerhouse, tailrace and trashrake
i | Structure | cy | 0 | 25 | 0 | From Pawtuxet 1m Pit Costs
ii | Intake | cy | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
iii | Tailrace | cy | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
h | Trashracks | sf | 0 | 400 | 0 | From Pawtuxet 1m Pit. Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 2000 | 444.6183 | 889.2366 | 4.3' diameter penstock. Includes: materials, shipping & installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p |  | cy |  |  | 0
q | Subtotal, Powerhouse/Intake |  |  |  | 1605.5001
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 455226.76 | 455.2268 | 900mm runner, estimated costs developed from recent projects
b | Shipping Handling & Installation |  | 1 | 114045.352 | 114.0454 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow verification
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 684.2721
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 1.5 | 60000 | 90 | Allowance for impacts from penstock alignment
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 157.5
9 | Licensing & Permitting
a | Consultations | year | 2 | 50000 | 100 | Allowance
b | Studies | year | 2 | 75000 | 150 | Alowance; assumes acceptance of standard instream flow settings
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 400
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Includes: sectionalizers, transformers, disconnect switch. From Interconnection Costs (Fostiak Eng. 2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 256197.7783 | 256.1978 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 436.1978
Totals
1 | General |  |  |  | 177
2 | Powerhouse/Intake |  |  |  | 1605.5001
3 | Equipment |  |  |  | 684.2721
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 157.5
9 | Licensing & Permitting |  |  |  | 400
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 3202.4722
12 | Indirect Costs |  |  |  | 436.1978
| Subtotal |  |  |  | 3638.67
13 | Contingency |  | 3638670.0074 | 20% | 727.734
| Grand Total |  |  |  | 4366.404

## Costs B (1-2 min flow)
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments |  | Notes: 12/14/10
1 | General | [6 empty] | Cost Base = Blackstone 3m Pit 9/13/10. Red values and notes indicate changes from base.
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance |  | Assumes - 1/2 instream flows 176 kw installed 130 cfs hyd cap @ 22 ft head
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 8000 | 32 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 90000 | 90 | From Phase I Dam Repair Costs (MBP Consulting 2010)
f | Subtotal, General |  |  |  | 177
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 592939.8226 | 592.9398 | Includes: intake, powerhouse, tailrace and trashrake
i | Structure | cy | 0 | 25 | 0 | From Pawtuxet 1m Pit Costs
ii | Intake | cy | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
iii | Tailrace | cy | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
h | Trashracks | sf | 0 | 400 | 0 | From Pawtuxet 1m Pit. Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 2000 | 474.7627 | 949.5255 | Assumes 4.6' diameter penstock. Includes: materials, shipping & installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Other |  |  |  | 0
q | Subtotal, Powerhouse/Intake |  |  |  | 1682.4653
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 485209.76 | 485.2098 | Runner 950mm, Estimated costs developed from recent projects | 2.5
b | Shipping Handling & Installation |  | 1 | 120041.952 | 120.042 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow verification
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 720.2517
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 1.5 | 60000 | 90 | Allowance for impacts from penstock alignment
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 157.5
9 | Licensing & Permitting
a | Consultations | year | 3 | 50000 | 150 | Allowance
b | Studies | year | 2.5 | 75000 | 187.5 | Alowance; assumes instream flow studies
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 487.5
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Includes: sectionalizers, transformers, disconnect switch. From Interconnection Costs (Fostiak Eng. 2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 272233.3622 | 272.2334 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 452.2334
Totals
1 | General |  |  |  | 177
2 | Powerhouse/Intake |  |  |  | 1682.4653
3 | Equipment |  |  |  | 720.2517
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 157.5
9 | Licensing & Permitting |  |  |  | 487.5
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 3402.917
12 | Indirect Costs |  |  |  | 452.2334
| Subtotal |  |  |  | 3855.1504
13 | Contingency |  | 3855150.3904 | 20% | 771.0301
| Grand Total |  |  |  | 4626.1805

## Costs B (no min flow)
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments
1 | General
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 8000 | 32 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 90000 | 90 | From Phase I Dam Repair Costs (MBP Consulting 2010)
f | Subtotal, General |  |  |  | 177
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 677586.0247 | 677.586 | Includes: intake, powerhouse, tailrace and trashrake
i | Structure | cy | 0 | 25 | 0 | From Pawtuxet 1m Pit Costs
ii | Intake | cy | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
iii | Tailrace | cy | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
h | Trashracks | sf | 0 | 400 | 0 | From Pawtuxet 1m Pit. Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 2000 | 614.0245 | 1228.049 | 5.8' diameter penstock. Includes: material, transporation and installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Other |  |  |  | 0
q | Subtotal, Powerhouse/Intake |  |  |  | 2045.635
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 701857.76 | 701.8578 | Runner 1.25m, estimated costs developed from recent projects | 2.5
b | Shipping Handling & Installation |  | 1 | 163371.552 | 163.3716 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow verification
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 980.2293
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 1.5 | 60000 | 90 | Allowance for impacts from penstock alignment
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 157.5
9 | Licensing & Permitting
a | Consultations | year | 3 | 50000 | 150 | Allowance
b | Studies | year | 2.5 | 75000 | 187.5 | Alowance; assumes instream flow studies
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 487.5
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Includes: sectionalizers, transformers, disconnect switch. From Interconnection Costs (Fostiak Eng. 2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 322085.1481 | 322.0851 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 502.0851
Totals
1 | General |  |  |  | 177
2 | Powerhouse/Intake |  |  |  | 2045.635
3 | Equipment |  |  |  | 980.2293
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 157.5
9 | Licensing & Permitting |  |  |  | 487.5
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 4026.0644
12 | Indirect Costs |  |  |  | 502.0851
| Subtotal |  |  |  | 4528.1495
13 | Contingency |  | 4528149.4996 | 20% | 905.6299
| Grand Total |  |  |  | 5433.7794

## Costs C
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments | Notes: 12/17/10
1 | General
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance | Assumes - 280 kw installed cap 114 cfs hyd cap 36.6 ft head 33% CF
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 8000 | 32 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 90000 | 90 | Phase I Dam Repair Cost (MBP Consulting)
f | Subtotal, General |  |  |  | 177
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 576263.5453 | 576.2635 | Includes: intake, powerhouse, tailrace and trashrake
i | Structure | cy | 0 | 100 | 0 | From Cargill Falls
ii | Intake | cy | 0 | 100 | 0 | From Cargill Falls
iii | Tailrace | cy | 0 | 100 | 0 | From Cargill Falls
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | Assume 40'x25' from Cargill Falls
h | Trashracks | sf | 0 | 400 | 0 | Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 2300 | 444.6183 | 1022.6221 | 4.3' diameter penstock. Includes: materials, shipping & installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Other |  |  |  | 0
q | Subtotal, Powerhouse/Intake |  |  |  | 1738.8856
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 455226.76 | 455.2268 | 900mm runner, estimated costs developed from recent projects
b | Shipping Handling & Installation |  | 1 | 114045.352 | 114.0454 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow verification
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 684.2721
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 3 | 60000 | 180 | Allowance for impacts from penstock and tailrace alignment
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 247.5
9 | Licensing & Permitting
a | Consultations | year | 3 | 50000 | 150 | Allowance
b | Studies | year | 2 | 75000 | 150 | Alowance; assumes acceptance of standard instream flow settings
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 450
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Includes: sectionalizers, transformers, disconnect switch. From Interconnection Costs (Fostiak Eng. 2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 278068.6172 | 278.0686 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 458.0686
Totals
1 | General |  |  |  | 177
2 | Powerhouse/Intake |  |  |  | 1738.8856
3 | Equipment |  |  |  | 684.2721
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 247.5
9 | Licensing & Permitting |  |  |  | 450
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 3475.8577
12 | Indirect Costs |  |  |  | 458.0686
| Subtotal |  |  |  | 3933.9263
13 | Contingency |  | 3933926.332 | 20% | 786.7853
| Grand Total |  |  |  | 4720.7116

## Costs C (1-2 min flow)
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments |  | Notes: 12/17/10
1 | General
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance |  | Assumes - 1/2 instream flows 313 kw installed cap 130 cfs hyd cap 36.6 ft head 40% CF
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 8000 | 32 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 90000 | 90 | Phase I Dam Repair Cost (MBP Consulting)
f | Subtotal, General |  |  |  | 177
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 592939.8226 | 592.9398 | Includes: intake, powerhouse, tailrace and trashrake
i | Structure | cy | 0 | 100 | 0 | From Cargill Falls
ii | Intake | cy | 0 | 100 | 0 | From Cargill Falls
iii | Tailrace | cy | 0 | 100 | 0 | From Cargill Falls
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | Assume 40'x25' from Cargill Falls
h | Trashracks | sf | 0 | 400 | 0 | Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 2300 | 474.7627 | 1091.9543 | Assumes 4.6' diameter penstock. Includes: materials, shipping & installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Other |  |  |  | 0
q | Subtotal, Powerhouse/Intake |  |  |  | 1824.8941
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 485209.76 | 485.2098 | 950mm, Costs developed from recent projects | 2.5
b | Shipping Handling & Installation |  | 1 | 120041.952 | 120.042 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow verification
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 720.2517
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 3 | 60000 | 180 | Allowance for impacts from penstock and tailrace alignment
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 247.5
9 | Licensing & Permitting
a | Consultations | year | 3 | 50000 | 150 | Allowance
b | Studies | year | 3 | 75000 | 225 | Alowance; assumes instream flow studies
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance |  |  | 120000
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 525
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Includes: sectionalizers, transformers, disconnect switch. From Interconnection Costs (Fostiak Eng. 2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 293827.6682 | 293.8277 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 473.8277
Totals
1 | General |  |  |  | 177
2 | Powerhouse/Intake |  |  |  | 1824.8941
3 | Equipment |  |  |  | 720.2517
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 247.5
9 | Licensing & Permitting |  |  |  | 525
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 3672.8459
12 | Indirect Costs |  |  |  | 473.8277
| Subtotal |  |  |  | 4146.6735
13 | Contingency |  | 4146673.5203 | 20% | 829.3347
| Grand Total |  |  |  | 4976.0082

## Costs C (no min flow)
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments |  | Notes: 12/17/10
1 | General
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance |  | Assumes - no instream flow 288 kw installed cap 213 cfs hyd cap 36.6 ft head 42% CF
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 8000 | 32 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 90000 | 90 | Phase I Dam Repair Cost (MBP Consulting)
f | Subtotal, General |  |  |  | 177
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 677586.0247 | 677.586 | Includes: intake, powerhouse, tailrace and trashrake
i | Structure | cy | 0 | 100 | 0 | From Cargill Falls
ii | Intake | cy | 0 | 100 | 0 | From Cargill Falls
iii | Tailrace | cy | 0 | 100 | 0 | From Cargill Falls
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | Assume 40'x25' from Cargill Falls
h | Trashracks | sf | 0 | 400 | 0 | Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 2300 | 614.0245 | 1412.2564 | 5.8' diameter penstock. Includes: material, transporation and installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Other |  |  |  | 0
q | Subtotal, Powerhouse/Intake |  |  |  | 2229.8424
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 701857.76 | 701.8578 | Runner 1.25m, estimated costs developed from recent projects | 2.5
b | Shipping Handling & Installation |  | 1 | 163371.552 | 163.3716 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow verification
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 980.2293
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 3 | 60000 | 180 | Allowance for impacts from penstock and tailrace alignment
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 247.5
9 | Licensing & Permitting
a | Consultations | year | 3 | 50000 | 150 | Allowance
b | Studies | year | 3 | 75000 | 225 | Alowance; assumes instream flow studies
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance |  |  | 120000
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 525
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Includes: sectionalizers, transformers, disconnect switch. From Interconnection Costs (Fostiak Eng. 2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 347021.7363 | 347.0217 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 527.0217
Totals
1 | General |  |  |  | 177
2 | Powerhouse/Intake |  |  |  | 2229.8424
3 | Equipment |  |  |  | 980.2293
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 247.5
9 | Licensing & Permitting |  |  |  | 525
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 4337.7717
12 | Indirect Costs |  |  |  | 527.0217
| Subtotal |  |  |  | 4864.7934
13 | Contingency |  | 4864793.44 | 20% | 972.9587
| Grand Total |  |  |  | 5837.7521

## Costs C - Francis Refurb
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments | Notes: 12/17/10
1 | General | [5 empty] | Cost Base = Blackstone 3m Pit 9/13/10. Red values and notes indicate changes from base.
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance | Assumes - Upgrade/Modernize existing Francis Unit 242 kw installed cap 102 cfs hyd cap 30% CF 36.6 ft GH
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 8000 | 32 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 90000 | 90 | Phase I Dam Repair Cost (MBP Consulting)
f | Subtotal, General |  |  |  | 177
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 100000 | 100 | Includes: intake, trashracks & powerhouse repairs
i | Structure | cy | 0 | 100 | 0 | Refurbishment Estimate
ii | Intake | cy | 0 | 100 | 0 | Refurbishment Estimate
iii | Tailrace | cy | 0 | 100 | 0 | Refurbishment Estimate
d | Demolition |  | 0 | 10000 | 0 | Refurbishment Estimate
e | Dewatering | week | 0 | 1000 | 0 | Refurbishment Estimate
f | Concrete | cy | 0 | 750 | 0 | Refurbishment Estimate
g | Superstructure, Decking | sf | 0 | 100 | 0 | Refurbishment Estimate
h | Trashracks | sf | 0 | 400 | 0 | Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 2300 | 444.6183 | 1022.6221 | 4.3' diameter penstock. Includes: material, shipping & installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Trashrake |  | 1 | 150000 | 150
q | Subtotal, Powerhouse/Intake |  |  |  | 1412.6221
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 400000 | 400 | Allowance
b | Shipping Handling & Installation |  | 1 | 103000 | 103 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow verification
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 618
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 3 | 60000 | 180 | Allowance for impacts from penstock and tailrace alignment
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 247.5
9 | Licensing & Permitting
a | Consultations | year | 3 | 50000 | 150 | Allowance
b | Studies | year | 2 | 75000 | 150 | Alowance; assumes acceptance of standard instream flow settings
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 450
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Includes: sectionalizers, transformers, disconnect switch. From Interconnection Costs (Fostiak Eng. 2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 246665.7646 | 246.6658 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 426.6658
Totals
1 | General |  |  |  | 177
2 | Powerhouse/Intake |  |  |  | 1412.6221
3 | Equipment |  |  |  | 618
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 247.5
9 | Licensing & Permitting |  |  |  | 450
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 3083.3221
12 | Indirect Costs |  |  |  | 426.6658
| Subtotal |  |  |  | 3509.9878
13 | Contingency |  | 3509987.8222 | 20% | 701.9976
| Grand Total |  |  |  | 4211.9854

## Costs D
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments | Notes: 12/17/10
1 | General | [5 empty] | Cost Base = Blackstone 3m Pit 9/13/10. Red values and notes indicate changes from base.
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance | Assumes - 120 kw installed 213 hyd cap 40% CF 8.4 ft GH
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 0.5 | 8000 | 4 | Allowance
d | E&S Control | ft. | 100 | 10 | 1 | Allowance
e | Dam Repairs |  | 1 | 50000 | 50 | Phase I Dam Repair Cost Est. (MBP Consulting 2010)
f | Subtotal, General |  |  |  | 90
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 677586.0247 | 677.586 | Includes: intake, powerhouse, tailrace and trashrake
i | Structure | cy | 0 | 25 | 0 | From Pawtuxet 1m Pit Costs
ii | Intake | cy | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
iii | Tailrace | cy | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
h | Trashracks | sf | 0 | 400 | 0 | From Pawtuxet 1m Pit. Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Sluice gate |  | 1 | 20000 | 20
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Other |  |  |  | 0
q | Subtotal, Powerhouse/Intake |  |  |  | 837.586
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 701857.76 | 701.8578 | Runner 1.25m, estimated costs developed from recent projects
b | Shipping Handling & Installation |  | 1 | 163371.552 | 163.3716 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow verification
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 980.2293
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 20000 | 20 | Allowance
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 0.5 | 60000 | 30 | Allowance
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 77.5
9 | Licensing & Permitting
a | Consultations | year | 2 | 50000 | 100 | Allowance
b | Studies | year | 0.5 | 75000 | 37.5 | Allowance
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 287.5
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 |  | 0
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 20
11 | Interconnection
a | Clear & Grub | acre | 0.5 | 8000 | 4 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Includes: sectionalizers, transformers, disconnect switch. From Interconnection Costs (Fostiak Eng. 2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 136
12 | Indirect Costs
a | A/E |  | 1 | 194305.2269 | 194.3052 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 374.3052
Totals
1 | General |  |  |  | 90
2 | Powerhouse/Intake |  |  |  | 837.586
3 | Equipment |  |  |  | 980.2293
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 77.5
9 | Licensing & Permitting |  |  |  | 287.5
10 | Land & Land Rights |  |  |  | 20
11 | Interconnection |  |  |  | 136
| Subtotal, Directs |  |  |  | 2428.8153
12 | Indirect Costs |  |  |  | 374.3052
| Subtotal |  |  |  | 2803.1206
13 | Contingency |  | 2803120.5636 | 20% | 560.6241
| Grand Total |  |  |  | 3363.7447

## Costs E
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments | Notes: 12/17/10
1 | General | [5 empty] | Cost Base = Blackstone 3m Pit 9/13/10. Red values and notes indicate changes from base.
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance | Assumes - New doble regulated Kaplan 200 kw installed cap 114 hyd cap 32% CF 26.2 ft GH
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 6200 | 24.8 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 50000 | 50 | Phase I Dam Repair Cost (MBP Consulting)
f | Subtotal, General |  |  |  | 129.8
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 576263.5453 | 576.2635 | Includes: intake, powerhouse, tailrace and trashrake
i | Structure | cy | 0 | 100 | 0 | From Cargill Falls
ii | Intake | cy | 0 | 100 | 0 | From Cargill Falls
iii | Tailrace | cy | 0 | 100 | 0 | From Cargill Falls
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | Assume 40'x25' from Cargill Falls
h | Trashracks | sf | 0 | 400 | 0 | Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 300 | 444.6183 | 133.3855 | 4.3' diameter penstock. Includes: materials, shipping & installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p |  | ea |  |  | 0
q | Subtotal, Powerhouse/Intake |  |  |  | 849.649
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 455226.76 | 455.2268 | 900 mm runner, Estimated costs developed from recent projects
b | Shipping Handling & Installation |  | 1 | 114045.352 | 114.0454 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow verification
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 684.2721
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 1.5 | 60000 | 90 | Allowance for impacts from tailrace
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 157.5
9 | Licensing & Permitting
a | Consultations | year | 2 | 50000 | 100 | Allowance
b | Studies | year | 2 | 75000 | 150 | Alowance; assumes acceptance of standard instream flow settings
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 400
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Fostiak Eng. (2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 191953.6914 | 191.9537 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 371.9537
Totals
1 | General |  |  |  | 129.8
2 | Powerhouse/Intake |  |  |  | 849.649
3 | Equipment |  |  |  | 684.2721
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 157.5
9 | Licensing & Permitting |  |  |  | 400
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 2399.4211
12 | Indirect Costs |  |  |  | 371.9537
| Subtotal |  |  |  | 2771.3748
13 | Contingency |  | 2771374.8345 | 20% | 554.275
| Grand Total |  |  |  | 3325.6498

## Costs E (1-2 min flow)
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments | Notes: 12/17/10
1 | General | [5 empty] | Cost Base = Blackstone 3m Pit 9/13/10. Red values and notes indicate changes from base.
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance | Assumes - New double regulated Kaplan 1/2 instream flows 234 kw installed cap 130 hyd cap 39% CF 26.2 ft GH
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 6200 | 24.8 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 50000 | 50 | Phase I Dam Repair Cost (MBP Consulting)
f | Subtotal, General |  |  |  | 129.8
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 592939.8226 | 592.9398 | Includes: intake, powerhouse, tailrace and trashrake
i | Structure | cy | 0 | 100 | 0 | From Cargill Falls
ii | Intake | cy | 0 | 100 | 0 | From Cargill Falls
iii | Tailrace | cy | 0 | 100 | 0 | From Cargill Falls
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | Assume 40'x25' from Cargill Falls
h | Trashracks | sf | 0 | 400 | 0 | Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 300 | 474.7627 | 142.4288 | Assumes 4.6' diameter penstock. Includes: materials, shipping & installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Other |  |  |  | 0
q | Subtotal, Powerhouse/Intake |  |  |  | 875.3686
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 485209.76 | 485.2098 | 950mm runner, estimated costs developed from recent projects
b | Shipping Handling & Installation |  | 1 | 120041.952 | 120.042 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow verification
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 720.2517
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 1.5 | 60000 | 90 | Allowance for impacts from tailrace alignment
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 157.5
9 | Licensing & Permitting
a | Consultations | year | 3 | 50000 | 150 | Allowance
b | Studies | year | 2.5 | 75000 | 187.5 | Alowance; assumes instream flow studies
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 487.5
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Fostiak Eng. (2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 203889.6287 | 203.8896 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 383.8896
Totals
1 | General |  |  |  | 129.8
2 | Powerhouse/Intake |  |  |  | 875.3686
3 | Equipment |  |  |  | 720.2517
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 157.5
9 | Licensing & Permitting |  |  |  | 487.5
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 2548.6204
12 | Indirect Costs |  |  |  | 383.8896
| Subtotal |  |  |  | 2932.51
13 | Contingency |  | 2932509.9873 | 20% | 586.502
| Grand Total |  |  |  | 3519.012

## Costs E (no min flow)
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments |  | Notes: 12/17/10
1 | General | [6 empty] | Cost Base = Blackstone 3m Pit 9/13/10. Red values and notes indicate changes from base.
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance |  | Assumes - New double regulated Kaplan no instream flows 383 kw installed cap 213 hyd cap 40% CF 26.2 ft GH
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 6200 | 24.8 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 50000 | 50 | Phase I Dam Repair Cost (MBP Consulting)
f | Subtotal, General |  |  |  | 129.8
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 677586.0247 | 677.586 | Includes: intake, powerhouse, tailrace and trashrake
i | Structure | cy | 0 | 100 | 0 | From Cargill Falls
ii | Intake | cy | 0 | 100 | 0 | From Cargill Falls
iii | Tailrace | cy | 0 | 100 | 0 | From Cargill Falls
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | Assume 40'x25' from Cargill Falls
h | Trashracks | sf | 0 | 400 | 0 | Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 300 | 614.0245 | 184.2074 | 5.8' diameter penstock. Includes: material, transporation and installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance | b
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Other | ea |  |  | 0
q | Subtotal, Powerhouse/Intake |  |  |  | 1001.7934
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 701857.76 | 701.8578 | Runner 1.25m, estimated costs developed from recent projects
b | Shipping Handling & Installation |  | 1 | 163371.552 | 163.3716 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow verification
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 980.2293
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 1.5 | 60000 | 90 | Allowance for impacts from tailrace alignment
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 157.5
9 | Licensing & Permitting
a | Consultations | year | 3 | 50000 | 150 | Allowance
b | Studies | year | 2.5 | 75000 | 187.5 | Alowance; assumes instream flow studies
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 487.5
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Fostiak Eng. (2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 234801.8151 | 234.8018 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 414.8018
Totals
1 | General |  |  |  | 129.8
2 | Powerhouse/Intake |  |  |  | 1001.7934
3 | Equipment |  |  |  | 980.2293
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 157.5
9 | Licensing & Permitting |  |  |  | 487.5
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 2935.0227
12 | Indirect Costs |  |  |  | 414.8018
| Subtotal |  |  |  | 3349.8245
13 | Contingency |  | 3349824.504 | 20% | 669.9649
| Grand Total |  |  |  | 4019.7894

## Costs E - Francis Repowered
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments | Notes: 12/17/10
1 | General | [5 empty] | Cost Base = Blackstone 3m Pit 9/13/10. Red values and notes indicate changes from base.
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance | Assumes - Upgrade/Modernize existing Francis Unit 200 kw installed cap 114 cfs hyd cap 30% CF 26.2 ft GH
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 6200 | 24.8 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 40000 | 40 | Phase I Dam Repair Cost (MBP Consulting)
f | Subtotal, General |  |  |  | 119.8
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Tailrace (cofferdam and excavation) |  |  |  | 25 | Allowance
c | Powerhouse Civil |  | 1 | 100000 | 100 | Allowance for intake, trashracks and powerhouse repairs
i | Structure | cy | 0 | 100 | 0 | Refurbishment Estimate
ii | Intake | cy | 0 | 100 | 0 | Refurbishment Estimate
iii | Tailrace | cy | 0 | 100 | 0 | Refurbishment Estimate
d | Demolition |  | 0 | 10000 | 0 | Refurbishment Estimate
e | Dewatering | week | 0 | 1000 | 0 | Refurbishment Estimate
f | Concrete | cy | 0 | 750 | 0 | Refurbishment Estimate
g | Superstructure, Decking | sf | 0 | 100 | 0 | Refurbishment Estimate
h | Trashracks | sf | 0 | 400 | 0 | Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 300 | 444.6183 | 133.3855 | Assumes 4.3' diameter penstock. Includes: materials, shipping & installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Trash Rake | ea | 1 | 150000 | 150 | Allowance
q | Subtotal, Powerhouse |  |  |  | 538.3855
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 400000 | 400 | Allowance
b | Shipping Handling & Installation |  | 1 | 103000 | 103 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 618
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 1 | 5000 | 5 | Allowance
d | Wetlands | acre | 1.5 | 60000 | 90 | Allowance for impacts from tailrace alignment
e | Recreation |  | 1 | 25000 | 25 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 167.5
9 | Licensing & Permitting
a | Consultations | year | 2 | 50000 | 100 | Allowance
b | Studies | year | 2 | 75000 | 150 | Alowance; assumes acceptance of standard instream flow settings
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 400
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Includes: sectionalizers, transformers, disconnect switch. From Interconnection Costs (Fostiak Eng. 2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 161750.8389 | 161.7508 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 341.7508
Totals
1 | General |  |  |  | 119.8
2 | Powerhouse/Intake |  |  |  | 538.3855
3 | Equipment |  |  |  | 618
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 167.5
9 | Licensing & Permitting |  |  |  | 400
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 2021.8855
12 | Indirect Costs |  |  |  | 341.7508
| Subtotal |  |  |  | 2363.6363
13 | Contingency |  | 2363636.3246 | 20% | 472.7273
| Grand Total |  |  |  | 2836.3636

## CostsE-FrancisRepow-no min flow
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments | Notes: 12/17/10
1 | General | [5 empty] | Cost Base = Blackstone 3m Pit 9/13/10. Red values and notes indicate changes from base.
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance | Assumes - Upgrade/Modernize existing Francis Unit 200 kw installed cap 114 cfs hyd cap 30% CF 26.2 ft GH
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 6200 | 24.8 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 40000 | 40 | Phase I Dam Repair Cost (MBP Consulting)
f | Subtotal, General |  |  |  | 119.8
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Tailrace (cofferdam and excavation) |  |  |  | 25 | Allowance
c | Powerhouse Civil |  | 1 | 100000 | 100 | Allowance for intake, trashracks and powerhouse repairs
i | Structure | cy | 0 | 100 | 0 | Refurbishment Estimate
ii | Intake | cy | 0 | 100 | 0 | Refurbishment Estimate
iii | Tailrace | cy | 0 | 100 | 0 | Refurbishment Estimate
d | Demolition |  | 0 | 10000 | 0 | Refurbishment Estimate
e | Dewatering | week | 0 | 1000 | 0 | Refurbishment Estimate
f | Concrete | cy | 0 | 750 | 0 | Refurbishment Estimate
g | Superstructure, Decking | sf | 0 | 100 | 0 | Refurbishment Estimate
h | Trashracks | sf | 0 | 400 | 0 | Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 300 | 551 | 165.3 | Assumes 5.21' diameter penstock. Includes: materials, shipping & installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Trash Rake | ea | 1 | 150000 | 150 | Allowance
q | Subtotal, Powerhouse |  |  |  | 570.3
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 475000 | 475 | Allowance for repowering 1.12m diameter Francis runner
b | Shipping Handling & Installation |  | 1 | 118000 | 118 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 708
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 1 | 5000 | 5 | Allowance
d | Wetlands | acre | 1.5 | 60000 | 90 | Allowance for impacts from tailrace alignment
e | Recreation |  | 1 | 25000 | 25 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 167.5
9 | Licensing & Permitting
a | Consultations | year | 2 | 50000 | 100 | Allowance
b | Studies | year | 2 | 75000 | 150 | Alowance; assumes acceptance of standard instream flow settings
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 400
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Includes: sectionalizers, transformers, disconnect switch. From Interconnection Costs (Fostiak Eng. 2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 171504 | 171.504 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 351.504
Totals
1 | General |  |  |  | 119.8
2 | Powerhouse/Intake |  |  |  | 570.3
3 | Equipment |  |  |  | 708
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 167.5
9 | Licensing & Permitting |  |  |  | 400
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 2143.8
12 | Indirect Costs |  |  |  | 351.504
| Subtotal |  |  |  | 2495.304
13 | Contingency |  | 2495304 | 20% | 499.0608
| Grand Total |  |  |  | 2994.3648

## Costs E - Francis Restored
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments | Notes: 12/17/10
1 | General | [5 empty] | Cost Base = Blackstone 3m Pit 9/13/10. Red values and notes indicate changes from base.
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance | Assumes - Restore existing Francis Unit 144 kw installed cap 102 cfs hyd cap 32% CF 26.2 ft GH
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 4 | 6200 | 24.8 | Allowance, includes penstock alignment
d | E&S Control | ft. | 2000 | 10 | 20 | Allowance, includes penstock alignment
e | Dam Repairs |  | 1 | 40000 | 40 | Phase I Dam Repair Cost (MBP Consulting)
f | Subtotal, General |  |  |  | 119.8
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 100000 | 100 | Allowance for intake, trashracks and powerhouse repairs
i | Structure | cy | 0 | 100 | 0 | From Cargill Falls
ii | Intake | cy | 0 | 100 | 0 | From Cargill Falls
iii | Tailrace | cy | 0 | 100 | 0 | From Cargill Falls
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | Assume 40'x25' from Cargill Falls
h | Trashracks | sf | 0 | 400 | 0 | Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Penstock | ft. | 300 | 369.1543 | 110.7463 | Assumes 3.7' diameter penstock. Includes: materials, shipping & installation
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | TrashRake | ea | 1 | 150000 | 150 | Allowance
q | Subtotal, Powerhouse |  |  |  | 500.7463
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 350000 | 350 | Estimated costs for restoration of 0.81 m diameter Francis runner
b | Shipping Handling & Installation |  | 1 | 93000 | 93 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | Fostiak Eng. (2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 558
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 40000 | 40 | Allowance for monitoring
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 1 | 5000 | 5 | Allowance
d | Wetlands | acre | 1.5 | 60000 | 90 | Allowance for impacts from tailrace restoration
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 162.5
9 | Licensing & Permitting
a | Consultations | year | 2 | 50000 | 100 | Allowance
b | Studies | year | 2 | 75000 | 150 | Alowance; assumes acceptance of standard instream flow settings
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 400
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 | 20000 | 20 | Allowance for penstock alignment
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 40
11 | Interconnection
a | Clear & Grub | acre | 1 | 6200 | 6.2 | Allowance
b | New Line |  | 1 | 52000 | 52 | Fostiak Eng. (2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Fostiak Eng. (2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 138.2
12 | Indirect Costs
a | A/E |  | 1 | 153539.7035 | 153.5397 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 333.5397
Totals
1 | General |  |  |  | 119.8
2 | Powerhouse/Intake |  |  |  | 500.7463
3 | Equipment |  |  |  | 558
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 162.5
9 | Licensing & Permitting |  |  |  | 400
10 | Land & Land Rights |  |  |  | 40
11 | Interconnection |  |  |  | 138.2
| Subtotal, Directs |  |  |  | 1919.2463
12 | Indirect Costs |  |  |  | 333.5397
| Subtotal |  |  |  | 2252.786
13 | Contingency |  | 2252785.9971 | 20% | 450.5572
| Grand Total |  |  |  | 2703.3432

## Costs F
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments | Notes: 12/17/10
1 | General | [5 empty] | Cost Base = Blackstone 3m Pit 9/13/10. Red values and notes indicate changes from base.
a | Mob/Demob |  | 1 | 25000 | 25 | Allowance | Assumes - 136 kw installed capacity 286 cfs max turbine flow based on 8' gross head
b | Site Prep |  | 1 | 10000 | 10 | Allowance
c | Clear & Grub | acre | 0.5 | 8000 | 4 | Allowance
d | E&S Control | ft. | 100 | 10 | 1 | Allowance
e | Dam Repairs |  | 1 | 20000 | 20 | From Phase I Dam Repair Costs (MBP Consulting 2010)
f | Subtotal, General |  |  |  | 60
2 | Powerhouse/Intake
a | Coffer dam, Pond |  |  |  | 100 | Allowance
b | Cofferdam, Tailrace |  |  |  | 10 | Allowance
c | Powerhouse Civil |  | 1 | 677586.0247 | 677.586 | Includes: intake, powerhouse, tailrace and trashrake
i | Structure | cy | 0 | 25 | 0 | From Pawtuxet 1m Pit Costs
ii | Intake | cy | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
iii | Tailrace | cy | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
d | Demolition |  | 0 | 10000 | 0 | Allowance
e | Dewatering | week | 0 | 1000 | 0 | From Cargill Falls
f | Concrete | cy | 0 | 750 | 0 | Allowance
g | Superstructure, Decking | sf | 0 | 100 | 0 | From Pawtuxet 1m Pit Costs
h | Trashracks | sf | 0 | 400 | 0 | From Pawtuxet 1m Pit. Check sizing for approach velocity target of 2 fps
i | Trashrake |  | 0 | 150000 | 0 | Allowance for automatic rake
j | Draft Tube gates |  | 0 | 15000 | 0 | Allowance
k | Sluice gate |  | 1 | 20000 | 20
l | Misc. metals |  | 1 | 5000 | 5 | Allowance
m | HVAC |  | 1 | 10000 | 10 | Allowance
n | Auxilliary Mechanical |  | 1 | 10000 | 10 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p | Other |  |  |  | 0
q | Subtotal, Powerhouse/Intake |  |  |  | 837.586
3 | Equipment
a | Turbine, generator, & governor |  | 1 | 701857.76 | 701.8578 | Runner 1.25m, estimated costs developed from recent projects
b | Shipping Handling & Installation |  | 1 | 163371.552 | 163.3716 | 20% of equipment costs
c | Switchgear |  | 1 | 20000 | 20 | From Interconnection Costs (Fostiak Eng. 2010)
d | Instrumentation & Controls |  | 1 | 50000 | 50 | Allowance, includes license min flow verification
e | Station Service, MCC |  | 1 | 20000 | 20 | Allowance
f | Protection |  | 1 | 25000 | 25 | Allowance
g | Subtotal, Equipment |  |  |  | 980.2293
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 20000 | 20 | Allowance
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included in Instrumentation & Controls
d | Wetlands | acre | 0.5 | 60000 | 30 | Allowance
e | Recreation |  | 1 | 20000 | 20 | Allowance
f | Cultural |  | 1 | 7500 | 7.5 | Allowance
g | Subtotal, PM&E |  |  |  | 77.5
9 | Licensing & Permitting
a | Consultations | year | 2 | 50000 | 100 | Allowance
b | Studies | year | 0.5 | 75000 | 37.5 | Allowance
c | Draft FERC Application |  | 1 | 50000 | 50 | Allowance
d | Final FERC Application |  | 1 | 25000 | 25 | Allowance
e | Legal review |  | 1 | 25000 | 25 | Allowance
f | Non-FERC Permits |  | 1 | 50000 | 50 | Allowance for: WQC, Wetlands, S. 106, S. 404, CZM, etc.
g | Subtotal, Lic. & Permitting |  |  |  | 287.5
10 | Land & Land Rights
a | Flowage rights |  | 1 | 5000 | 5 | Allowance
b | Project works, land in fee |  | 1 |  | 0
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 1 | 10000 | 10 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 20
11 | Interconnection
a | Clear & Grub | acre | 0.5 | 8000 | 4 | Allowance
b | New Line |  | 1 | 15000 | 15 | From Interconnection Costs (Fostiak Eng. 2010)
c | Metering |  | 1 | 10000 | 10 | Allowance
c | Switchyard |  | 1 | 50000 | 50 | Includes: sectionalizers, transformers, disconnect switch. From Interconnection Costs (Fostiak Eng. 2010)
d | Consultations |  | 1 | 20000 | 20 | Allowance
f | Subtotal, Interconnection |  |  |  | 99
12 | Indirect Costs
a | A/E |  | 1 | 188945.2269 | 188.9452 | 8% of Direct Costs
b | Construction Management |  | 1 | 25000 | 25 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 35000 | 35 | Design Report, Status Reports
e | Owner's Admin & Overhead |  | 1 | 100000 | 100 | Allowance
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 368.9452
Totals
1 | General |  |  |  | 60
2 | Powerhouse/Intake |  |  |  | 837.586
3 | Equipment |  |  |  | 980.2293
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 77.5
9 | Licensing & Permitting |  |  |  | 287.5
10 | Land & Land Rights |  |  |  | 20
11 | Interconnection |  |  |  | 99
| Subtotal, Directs |  |  |  | 2361.8153
12 | Indirect Costs |  |  |  | 368.9452
| Subtotal |  |  |  | 2730.7606
13 | Contingency |  | 2730760.5636 | 20% | 546.1521
| Grand Total |  |  |  | 3276.9127

## Costs Min Flow Unit
No. | Item | Unit | Qty | Rate | Amount ($1,000's) | Comments
1 | General | [6 empty] | Notes: 12/14/10
a | Mob/Demob |  | 0 | 25000 | 0 | Included on Costs B, C & E |  | Cost Base = Blackstone 3m Pit 9/13/10 & Robert King Hydro 8/7/09. Red values and notes indicate changes from base.
b | Site Prep |  | 1 | 10000 | 10 | Allowance |  | Modified to reflect incremental costs for 10 Mile R. options with bypass reach & min flow unit. Anticipate some site specific modifications that can be developed on individual proforma sheets.
c | Clear & Grub | acre | 0.25 | 8000 | 2 | Allowance
d | E&S Control | ft. | 200 | 10 | 2 | Allowance
e | Dam Repairs |  | 0 |  | 0 | Included in Individual Cost Sheets
f | Subtotal, General |  |  |  | 14
2 | Powerhouse/Intake
a | Coffer dam, Pond |  | 0 | 100000 | 0 | Included on Costs B, C & E
b | Coffer dam, Tailrace |  | 1 | 10000 | 10 | Allowance
c | Excavation |  | 0 |  | 0
i | Structure | cy | 0 | 100 | 0 | Allowance; From Dexter Russell
ii | Intake | cy | 40 | 100 | 4 | Allowance; From Dexter Russell
iii | Tailrace | cy | 100 | 100 | 10 | Allowance; From Dexter Russell
d | Demolition |  | 1 | 5000 | 5 | Allowance
e | Dewatering | week | 2 | 1000 | 2 | Allowance; From Dexter Russell
f | Concrete | cy | 10 | 500 | 5 | Allowance; From Dexter Russell
g | Superstructure, Decking | sf | 275 | 100 | 27.5 | Allowance; From Dexter Russell
h | Trashracks | sf | 0 | 100 | 0 | Included on Costs B, C & E
i | Trashrake |  | 0 | 150000 | 0 | Included on Costs B, C & E
j | Draft Tube gates |  | 0 | 5000 | 0 | Allowance; From Dexter Russell
k | Sluice gate |  | 0 | 20000 | 0
l | Misc. metals |  | 1 | 3000 | 3 | Allowance; From Dexter Russell
m | HVAC |  | 0 | 10000 | 0
n | Auxilliary Mechanical |  | 1 | 5000 | 5 | Allowance
o | Lighting, auxilliary electrical |  | 1 | 5000 | 5 | Allowance
p |  |  | 0 | 500 | 0
q | Subtotal, Powerhouse |  |  |  | 76.5
3 | Equipment
a | Turbine, generator, governor, controls, breaker & protection |  | 1 | 50000 | 50 | Mavel TM-3 Siphon Unit (qoute from 6/09) 10 cfs hyd cap. | 2.5
b | Shipping Handling & Installation |  | 1 | 15000 | 15 | 20% of equipment costs
c | Switchgear |  | 1 | 5000 | 5 | Allowance; From Dexter Russell
d | I&C |  | 1 | 5000 | 5 | Allowance; From Dexter Russell
e | Station Service, MCC |  | 1 | 5000 | 5 | Allowance; From Dexter Russell
f | Draft Tube extension |  | 1 | 10000 | 10 | Allowance; From Dexter Russell
g | Subtotal, Equipment |  |  |  | 90
4 | Spillway
a | Coffer Dams | sf |  | 40 | 0 | Allowance
b | Excavation | cy |  | 15 | 0 | Allowance
c | Spillway Concrete | cy |  | 450 | 0 | Allowance
d | Pneumatic flashboards |  |  |  | 0
e | Other |  |  |  | 0
f | Subtotal, Spillway |  |  |  | 0
5 | East (left) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, East Dike |  |  |  | 0
5 | West (right) Dike
a | Access |  |  | 1000 | 0 | Allowance
b | E&S Control | ft. |  | 5 | 0 | Assume 50-ft. of length
c | Clear & grub | acre |  | 6201 | 0 | Allowance
d | Excavation | cy |  | 15 | 0 | Assume 50-ft. of length
e | Dike restoration | cy |  | 40 | 0 | Assume 50-ft. of length
f | Other |  |  |  | 0
g | Subtotal, West Dike |  |  |  | 0
7 | Canal
a | Clear & grub | acre |  | 6200 | 0 | Allowance
b | Excavation | cy |  | 20 | 0 | Assume 1,000-ft. of length
c | Bank Restoration | cy |  | 40 | 0 | Assume 1,000-ft. of length
d | Concrete | cy |  | 450 | 0 | Allowance
d | Other |  |  |  | 0
e | Subtotal, Canal |  |  |  | 0
8 | PM&E Measures
a | Water Quality |  | 1 | 15000 | 15 | In addition to costs included on Costs B, C & E
b | D/S fish passage |  | 0 | 20000 | 0 | Assumes installed by others
c | Min flow verification |  | 0 | 5000 | 0 | Included on Costs B, C & E
d | Wetlands | acre | 0 | 60000 | 0 | Included on Costs B, C & E
e | Recreation |  | 0 | 7500 | 0 | Included on Costs B, C & E
f | Cultural |  | 0 | 7500 | 0 | Included on Costs B, C & E
g | Subtotal, PM&E |  |  |  | 15
9 | Licensing & Permitting
a | Consultations | year | 0 | 50000 | 0 | Included on Costs B, C & E
b | Studies | year | 0 | 75000 | 0 | Included on Costs B, C & E
c | Draft FERC Application |  | 0 | 50000 | 0 | Included on Costs B, C & E
d | Final FERC Application |  | 0 | 25000 | 0 | Included on Costs B, C & E
e | Legal review |  | 0 | 5000 | 0 | Included on Costs B, C & E
f | Non-FERC Permits |  | 0 | 50000 | 0 | Included on Costs B, C & E
g | Subtotal, Licensing & Permitting |  |  |  | 0
10 | Land & Land Rights
a | Flowage rights |  | 0 | 5000 | 0 | Allowance
b | Project works, land in fee |  | 0 |  | 0
c | Interconnection R.O.W. |  | 1 | 5000 | 5 | Allowance
d | Legal |  | 0 | 10000 | 0 | Allowance
e | Other |  |  |  | 0
f | Subtotal, Land |  |  |  | 5
11 | Interconnection
a | Clear & Grub | acre | 0 | 6200 | 0 | Included on individual proformas (see Interconnection Costs tab)
b | New Line |  | 4 | 5000 | 20 | In addition to costs included on Costs B, C & E
c | Metering |  | 0 | 10000 | 0 | Included on individual proformas (see Interconnection Costs tab)
c | Switchyard |  | 0 | 25000 | 0 | Included on individual proformas (see Interconnection Costs tab)
d | Other |  | 0 | 50000 | 0 | Included on individual proformas (see Interconnection Costs tab)
f | Subtotal, Interconnection |  |  |  | 20
12 | Indirect Costs
a | A/E |  | 1 | 17640 | 17.64 | 8% of Direct Costs
b | Construction Management |  | 1 | 10000 | 10 | Allowance
c | Testing |  | 1 | 20000 | 20 | geo-tech, concrete
d | FERC submittals |  | 1 | 10000 | 10 | In addition to costs included on Costs B, C & E
e | Owner's Admin & Overhead |  |  |  | 0
f | Other |  |  |  | 0
g | Subtotal, Indirects |  |  |  | 57.64
Totals
1 | General |  |  |  | 14
2 | Powerhouse/Intake |  |  |  | 76.5
3 | Equipment |  |  |  | 90
4 | Spillway |  |  |  | 0
5 | East (left) Dike |  |  |  | 0
5 | West (right) Dike |  |  |  | 0
7 | Canal |  |  |  | 0
8 | PM&E Measures |  |  |  | 15
9 | Licensing & Permitting |  |  |  | 0
10 | Land & Land Rights |  |  |  | 5
11 | Interconnection |  |  |  | 20 | See individual proforma sheets
| Subtotal, Directs |  |  |  | 220.5
12 | Indirect Costs |  |  |  | 57.64
| Subtotal |  |  |  | 278.14
13 | Contingency |  | 278140 | 20% | 55.628
| Grand Total |  |  |  | 333.768

## Phase I Dam Repairs
Dam | Repair Costs | General Maintenance Costs | TOTAL ($1,000's)
Omega | 10000 | 10000 | 20
Hunt's Mill | 40000 | 10000 | 50
Turner Reservoir | 30000 | 10000 | 40
Repair estimates from Phase I Inspection Rpt (MBP Consulting, 11/10)
General Maintenance costs are catch-up allowances

## Penstock Costs
Source | Length (FT) | Diameter (FT) | Cost (FOB) | 2010 Cost | Cost/FT
DB Cotton, Apr 2009 | 300 | 6 | 125000 | 128125 | 427.0833
Val, July 2011 | 300 | 7 | 144000 | 144000 | 480
DB Cotton, Apr 2009 | 1500 | 8 | 520000 | 533000 | 355.3333
DB Cotton, Apr 2009 | 300 | 10 | 185000 | 189625 | 632.0833
Val, July 2010 | 300 | 12 | 204000 | 204000 | 680
Values for Formula
[5 empty] | Cost/FT | Eq
DB Cotton, Apr 2009 | 300 | 6 | 125000 | 128125 | 427.0833 | 423.0225
Val, July 2011 | 300 | 7 | 144000 | 144000 | 480 | 486.4971
DB Cotton, Apr 2009 | 300 | 10 | 185000 | 189625 | 632.0833 | 628.0225
Val, July 2010 | 300 | 12 | 204000 | 204000 | 680 | 681.6241
Values for East Providence
| Dia (FT) | Material $/FT | Length FT | Material | Transp and Install | Total 2010 Costs
| 3.7 | 246.1029 | 1 | 246.1029 | 123.0514 | 369.1543
| 4.3 | 296.4122 | 1 | 296.4122 | 148.2061 | 444.6183
| 4.7 | 328.3218 | 1 | 328.3218 | 164.1609 | 492.4827
| 4.55 | 316.5085 | 1 | 316.5085 | 158.2542 | 474.7627
| 5.8 | 409.3497 | 1 | 409.3497 | 204.6748 | 614.0245
| 5.21 | 367.1154 | 1 | 367.1154 | 183.5577 | 550.6731
| 7 | 486.4971 | 1 | 486.4971 | 243.2486 | 729.7457
| 8 | 541.822 | 1 | 541.822 | 270.911 | 812.7329

## Pwrhse Cost Estimator
| Runner Diameter (mm) | Powerhouse Civil (items 2c-j) | 2010 Civil Cost | Formula
Pawtuxet | 1050 | 488279.4118 | 500486.3971 | 573809.1639
Pawtuxet | 1500 | 602419.1176 | 617479.5956 | 683820.5558
Cargill Falls | 1700 | 899966.617 | 922465.7824 | 722425.3746
Blackstone R. | 3000 | 805200.25 | 825330.2562 | 897612.0974
| 810 | 493766.5696
| 900 | 526263.5453
| 920 | 533042.6313
| 950 | 542939.8226
| 1250 | 627586.0247
Case | Runner Diameter (mm) | Runner Diameter (FT) | 2010 Civil Cost Formula + $50k for intake
B,C, E; w/ Qmin | 900 | 2.952 | 576263.5453
C2, E2, E3 | 920 | 3.0176 | 583042.6313
B,C, E; 1/2 Qmin | 950 | 3.116 | 592939.8226
A, F; and B,C, E; no Qmin | 1250 | 4.1 | 677586.0247

## TG Costs
No | Description | 2009 | 2010 |  |  | Diameter Bulb | 2010 Price ($1,000's) | Eq Price ($1,000's)
1 | Mavel 0.85M Bulb, Dbl Reg | 350 |  |  |  | 850 | 360 | 426.9938
2 | Mavel 1.29M Vert Kapl | 450 |  |  |  | 1050 | 500 | 550.4258
3 | Mavel 1.05M Bulb, Dbl Reg | 490 |  |  |  | 1290 | 900 | 735.5042
4 | Mavel 1.8M Vert Kapl | 1125 |  |  |  | 1800 | 1140 | 1262.6708
5 | Mavel 0.85M Vert Kapl | 400 | 650 | mm | 0.00035185 | 3000 | 3170 | 3221.2628
6 | Mavel 1.29 Bulb, Dbl Reg |  | 900 | bb | 60
7 | Mavel 1.8 Bulb, Dbl Reg |  | 1140 | b= | 293
|  |  |  | m= | 0.47059
|  | Dia | Price | Eq
| Dbl Reg Bulbs (esc 2009 by 2.5%) | 850 | 358.75 | 693 | 314.213
|  | 1050 | 502.25 | 787.1176 | 447.9167
|  | 1290 | 900 | 900.0588 | 645.5167
|  | 1500 | 998.8235 | 998.8824 | 851.6667
|  | 1800 | 1140 | 1140.0588 | 1200
|  | 3000 | 3166.6667 | 1704.7647 | 3226.6667
1900
2533.3333
Cost Calculator
| Input Diameter Bulb | 1250 | 701.8578 | 2010 Price ($1,000's)
| Runner Diameter (mm) | Cost
| 810 | 405.6674 | 405667.36
| 900 | 455.2268 | 455226.76
| 920 | 467.01 | 467009.96
| 950 | 485.2098 | 485209.76
| 1250 | 701.8578 | 701857.76

## Regulatory Costs
Licensing & Permitting Summary
Alternatives | Key Regulatory Drivers | Consultations (yrs) | Studies (yrs) | Costs ($1,000's)
A, D, F | Minimal Env. Impacts (bypass, stream flows & wetlands) | 2 | 0.5 | 288
B, E | Bypass, Wetland Impacts, Standard ABF | 2 | 2 | 400
C | Longer Bypass, More Wetland Impacts, Standard ABF | 3 | 2 | 450
B, E | Bypass, Wetland Impacts, Modified ABF | 3 | 2.5 | 488
C | Longer Bypass, More Wetland Impacts, Modified ABF | 3 | 3 | 525

## Interconnect Costs
ITEM / DESCRIPTION |  | INTERCONNECTION TO NATIONAL GRID
|  | Turner Reservoir (Single Circuit) |  |  |  | Hunt's Mill (Single Circuit) |  |  |  | Omega Pond (Single Circuit)
|  | Qty | Units | Unit Price | Total Price | Qty | Units | Unit Price | Total Price | Qty | Units | Unit Price | Total Price
1 | 13.8 kV Overhead Distribution Line | 0.33 | mi. | 100000 | 33000 | 0.52 | mi. | 100000 | 52000 | 0.15 | mi. | 100000 | 15000
2 | 13.8 kv Sectionalizers | 1 | ea | 10000 | 10000 | 1 | ea | 10000 | 10000 | 1 | ea | 10000 | 10000
3 | 13.8 kV Pole-Mounted Distribution Transformers | 3 | ea | 10000 | 30000 | 3 | ea | 10000 | 30000 | 3 | ea | 10000 | 30000
4 | 3-Phase Fused Disconnecting Switch | 1 | ea | 10000 | 10000 | 1 | ea | 10000 | 10000 | 1 | ea | 10000 | 10000
5 | Service Switchgear - Main disconnecting switch -Branch circuit breakers | 1 | ea | 20000 | 20000 | 1 | ea | 20000 | 20000 | 1 | ea | 20000 | 20000
| Total |  |  |  | 103000 |  |  |  | 122000 |  |  |  | 85000